# 0 · Tag glossary — what every signal name means

*Read this first, then keep it open. In the safety PLC every wire and signal has a short code called a tag. This page explains, in plain English, what each tag is and what its 1/0 value means. The other documents use these same tags and repeat a short description each time — this page is the full list.*

Two words you need:

Input = a signal coming *into* the PLC from a switch, button or sensor.

Output = a signal the PLC *sends out* to switch something on or off.

`1` (TRUE) = the signal is on / present. `0` (FALSE) = off / absent.

De-energise to trip = the *safe* state is OFF. If power is lost, the device

springs to its safe position by itself.

__________________________________________________

## A. Inputs — the doors and gates (position switches)

| Tag | What it is | 1 means | 0 means |
| --- | --- | --- | --- |
| BL10E-PS-GADC-01, -02, -03 | Three "closed" switches on the main personnel door ("General Access Door Closed") | door is shut | door is open |
| BL10E-PS-GADC-04, -05, -06 | Three "closed" switches on the entrance gate ("General Access Gate Closed") | gate is shut | gate is open |
| BL10E-PS-SADC-01…-05 | "Closed" switches on the service / maintenance door ("Service Access Door Closed") | door is shut | door is open |
| BL10E-PS-GADL-01, -02, -04, -05 | "Locked" switches that feel the bolt of the main door / gate ("General Access Door Locked") | door/gate is locked | not locked |
| BL10E-PS-SADL-01, -02 | "Locked" switches that feel the bolt of the service door ("Service Access Door Locked") | door is locked | not locked |

## B. Inputs — keys, card and buttons

| Tag | What it is | 1 / action |
| --- | --- | --- |
| BL10E-PS-KEY-01 | Electron-source enable key at the control panel (ZCP) | 1 = key turned ON |
| BL10E-PS-KEY-02 | Hutch enable key (needed to start a search) | 1 = key turned ON |
| BL10E-PS-KEY-03 | Electron-source enable key at the equipment rack | 1 = key turned ON |
| BL10E-PS-SCR-01 | Search card reader at the door | 1 = valid search card presented |
| BL10E-PS-BOB-01:A/:B … BOB-08:A/:B | The eight Beam-Off Buttons (emergency stop). Each button has two wires, channel :A and channel :B, for safety | 1 = button NOT pressed; 0 = pressed |
| BL10E-PS-ASB-01, -02, -03, -04 | Area-search buttons pressed in order while walking through the hutch | a press = value goes 0→1 |
| BL10E-PS-ASBF-01 | The final area-search button, next to the exit door | a press = 0→1 |
| BL10E-PS-LCRx-01 | Light curtain beam across the doorway (detects a person passing) | 1 = clear; 0 = beam broken |
| BL10E-PS-OR-01 | The Open / Reset button the operator presses to unlock and reset | a press = 0→1 |
| BL10E-PS-IOC-01-BOB:RESET | Control-room reset button for the beam-off-button latch | a press = 0→1 |
| BL10E-PS-IOC-01-RDMN:RESET | Control-room reset button for the radiation latch | a press = 0→1 |
| BL10E-PS-IOC-01-GAS:RESET | Control-room reset button for the oxygen/gas latch | a press = 0→1 |
| BL10E-PS-IOC-01-SYS:RESET | Control-room reset button for general system latches | a press = 0→1 |

## C. Inputs — the analogue sensors (they send a 4–20 mA signal)

| Tag | What it is |
| --- | --- |
| BL10E-PS-IT-01, -02, -03 | Current transmitters on the electron source (lines L1/L2/L3). A high reading means the source is electrically live |
| BL10E-PS-VT-01, -02, -03 | Voltage transmitters on the electron source (L1/L2/L3). High = source live |
| BL10E-PS-OXMON-01…-04 | Oxygen monitors in the hutch. A low reading means the air is unsafe to breathe |
| BL10E-PS-RDMND-01, -02 | Radiation monitors — accumulated dose |
| BL10E-PS-RDMNR-01, -02 | Radiation monitors — dose rate |

Each analogue sensor has three helper tags:

…_SP = the set-point (the level at which it trips).

…_HYST = the hysteresis (a small dead-band so it doesn't flicker on/off).

…_TRIP = the trip flag the PLC makes from the sensor: 1 = the limit has

been crossed (oxygen too low, or source live), 0 = normal.

…_OC / …_SC / …_CH_OK = wiring health (open-circuit / short-circuit / channel OK).

## D. Internal signals — the Safety Functions (SIFs)

Each safety function makes one main signal. Important: most of these are "permissives" — `1` = healthy / allowed, and they drop to `0` to trip.

| Tag | What it is | 1 means |
| --- | --- | --- |
| BL10E-SIF-01_TRIP | Main personnel door function | door is shut, OK to run |
| BL10E-SIF-02_TRIP | Service door function | service door shut, OK |
| BL10E-SIF-03_OUTPUT | "Source is really off, doors may unlock" permit | safe to unlock |
| BL10E-SIF-05_START | Search-start permit (card + keys + doors) | a search may begin |
| BL10E-SIF-06_TRIP / _OUTPUT | Search-complete proof (all doors shut) | search may finish |
| BL10E-SIF-07_OUTPUT | Beam-on master permit (locks confirmed + 180 s wait) | beam may come on |
| BL10E-SIF-08_TRIP | Beam-off-button function | no button pressed, OK |
| BL10E-SIF-09_TRIP | Radiation function | radiation normal, OK |
| BL10E-SIF-10_TRIP | Enable-key function | key on, OK |
| BL10E-SIF-11_TRIP | Oxygen function | oxygen OK |
| BL10E-SIF-13_TRIP | Gate function | gate shut, OK |

## E. Internal signals — the search "state" and its timers

| Tag | What it is |
| --- | --- |
| STATUS-OPEN / STATUS-OPEN_READY | The hutch is open (safe to enter) / ready to start a search |
| STATUS-START_SEARCH | A search has begun |
| STATUS-HUTCH_ENTERED | The searcher has stepped through the light curtain |
| STATUS-ASB1 … STATUS-ASB4 | Area-search buttons 1–4 have been pressed in order |
| STATUS-STANDBY | Search done, doors locked, waiting before beam |
| STATUS-BEAM_ON | The hazard (beam) is on |
| SEARCHED_AND_LOCKED | A memory bit: "search finished and doors locked." If broken, you must search again |
| SEARCH_TIMER_RUNNING / SEARCH_TIME_EXCEEDED | The overall 180-second search clock is running / has run out |
| LIGHT_CURTAIN_MONITORING | The light curtain is being watched for extra people |
| BEAM_DELAY_TIMER_END / _ELAPSED | The 180-second "radiation imminent" warning wait has finished |
| ABORT_SEARCH / ABORT_START | The search has been cancelled |
| T1-T2_TIMER_TRIP_LOW / _HIGH (and T2-T3 … T6-T7) | A step was done too fast (LOW, under 5 s) or too slow (HIGH, over 60 s) |

## F. Outputs — the things the PLC switches (all "de-energise to trip")

| Tag | What it is | 1 (energised) | 0 (safe) |
| --- | --- | --- | --- |
| BL10E-PS-CON-01:EN … CON-05:EN | Power contactors feeding the electron source | source powered (hazard live) | source isolated |
| BL10E-PS-CON-06:EN, -07, -08 | Power contactors for the 3-phase RF supply | RF powered | RF isolated |
| BL10E-PS-CON-09:EN, -10 | Power contactors for the 1-phase RF drive | RF drive powered | isolated |
| BL10E-PS-CON-0x:FB | Feedback wire from each contactor (an aux contact telling the PLC its real state) | (mirrors the contactor) | — |
| BL10E-PS-SOL-01 … SOL-06 | Lock solenoids — the bolts that lock the doors/gate | door locked | door unlocked |
| BL10E-PS-ANNOPN-01:A/:B | Hutch sign: "OPEN" (dual channel A/B) | sign lit | off |
| BL10E-PS-ANNRES-01:A/:B | Hutch sign: "RESTRICTED" | sign lit | off |
| BL10E-PS-ANNSTB-01:A/:B | Hutch sign: "STANDBY" | sign lit | off |
| BL10E-PS-ANNBON-01:A/:B | Hutch sign: "BEAM ON" | sign lit | off |
| BL10E-PS-SP01-0x / SP02-0x / SP03-0x | Beacons / sounders (warning lights and sirens) | sounding | off |
| BL10E-PS-BLUEL-01:A/:B … BLUEL-06 | Blue warning lights (radiation deterrent) | on | off |
| BL10E-PS-BONI-01:A/:B | "Beam On" indicator lamp | on | off |
| BL10E-PS-BOBI-01:A/:B … BOBI-05 | "Press Beam Off" indicators | on | off |
| BL10E-PS-SDVLN2 (valve SOVLN2-01) | Liquid-nitrogen shut-off valve | valve open (gas can flow) | valve closed (safe) |
| BL10E-PS-SOVLN2-01:OP / :CL | Valve position feedback: open switch / closed switch | that position reached | — |
| BL10E-PS-IND-01, -02, -03 | Oxygen traffic-light indicators (green/red) | green (air OK) | red (oxygen low) |
| BL10E-PS-WLT-01 | White lights inside the hutch | on | off |
| BL10E-PS-KEY-01:SOL / KEY-02:SOL | Key-trap solenoids that hold a key in place | key trapped | key released |

__________________________________________________

*Tip: when you see a tag in any document, the first part BL10E-PS- just means "Beamline 10E – Personnel Safety". The middle part is the device (e.g. GADC = General Access Door Closed), and the number is which one.*