# 2 · The hutch SEARCH sequence (T1 → T7 → Beam On)

*This document walks you through the search, one step at a time: what the searcher does, which tag makes each step advance, and what you should see happen next. It also lists the two timers and the things that abort a search.*

This is the heart of the system. It is SIF-04, built inside the PLC as a Sequential Function Chart (SFC). An SFC is just a step-by-step state machine: the program sits in one state (one step) at a time, and only moves on when a transition is met. A transition is the event — a button, a key, a timer — that moves you from one step to the next. We label the transitions T1, T2, T3 ….

A hutch is the shielded room that holds the hazard. To follow the tag names, see document 00 (the glossary).

__________________________________________________

## 2.1 Why a "search"

Before the radiation/RF hazard can be switched on, a trained person must physically walk through the whole hutch to confirm nobody is left inside. They must do it in a fixed order, inside strict time windows, and then lock the doors behind them. The PLC only lets the beam on if that exact routine is done correctly.

If the searcher does anything wrong — wrong button, too fast, too slow, or a door opens — the search aborts and they must start again.

This defends against the worst case: a person hiding or working in the hutch while a colleague switches the beam on.

__________________________________________________

## 2.2 The states (what the hutch is doing)

These are the real PLC state names. Each is a STATUS-* flag that reads 1 when the hutch is in that state. They come straight from the program (see document 03, the program logic reference).

OPEN ──▶ OPEN_READY ──▶ START_SEARCH ──▶ HUTCH_ENTERED ──▶ ASB1 ──▶ ASB2
                            (T1)              (T2)           (T3)     (T4)
                                                                       │
        OPEN ◀── BEAM_ON ◀── STANDBY ◀── ASB4 ◀── ASB3 ◀──────────────┘
        (T9)      (T8)         (T7)       (T6)     (T5)

| State (tag) | Plain meaning | Annunciator sign |
| --- | --- | --- |
| STATUS-OPEN | The hutch is open and safe to enter. Doors unlocked, no hazard | OPEN |
| STATUS-OPEN_READY | The hutch is ready to start a search: all doors closed and keys in | OPEN |
| STATUS-START_SEARCH | A search has begun; the service doors lock | RESTRICTED |
| STATUS-HUTCH_ENTERED | The searcher has stepped through the light curtain | RESTRICTED |
| STATUS-ASB1 … STATUS-ASB4 | Area-search buttons 1–4 have been pressed in order | RESTRICTED |
| STATUS-STANDBY | Search done, all doors locked, waiting before the beam | STANDBY |
| STATUS-BEAM_ON | The hazard (the beam) is on | BEAM ON |

__________________________________________________

## 2.3 The steps, one at a time

Read this table top to bottom. Each row is one transition Tn — the event that moves the SFC to the next state. For each step you get: (a) what the searcher physically does, (b) which tag/condition makes it advance, and (c) what happens and what to see next.

A few tags used below:

BL10E-PS-SCR-01 — the search card reader at the door. Reads 1 when a

valid search card is presented.

KEY-01 (BL10E-PS-KEY-01) — the electron-source enable key at the

control panel. 1 = key turned ON.

KEY-02 (BL10E-PS-KEY-02) — the hutch enable key needed to start a

search. 1 = key turned ON.

LCRx-01 (BL10E-PS-LCRx-01) — the light curtain, an invisible beam

across the doorway that detects a person passing. 1 = clear, 0 = broken.

ASB-01 … ASB-04 (BL10E-PS-ASB-01..04) — the four area-search buttons

you press in order while walking through the hutch. A press = 0→1.

ASBF-01 (BL10E-PS-ASBF-01) — the final area-search button, next to the

exit door. A press = 0→1.

SADC (BL10E-PS-SADC-*) — the service-door "closed" switches. 1 = the

service door is shut.

SEARCHED_AND_LOCKED — a memory bit meaning "search finished and doors

locked." If it is broken, you must search again.

| T | From → To | (a) What the searcher does | (b) Tag/condition that advances it | (c) What happens / what to see next |
| --- | --- | --- | --- | --- |
| T1 | STATUS-OPEN_READY → STATUS-START_SEARCH | Present the search card at BL10E-PS-SCR-01, and turn KEY-01 (electron source) and KEY-02 (hutch) to ON | Service doors shut (SADC = 1), and no beam-off latched (SIF-05, the search-start permit, is healthy) | Service doors lock; RESTRICTED sign on; speaker SP01 says "search in progress"; white lights WLT-01 on; the 180 s search timer starts |
| T2 | STATUS-START_SEARCH → STATUS-HUTCH_ENTERED | Walk through the light curtain once — a single pass | LCRx-01 goes 1→0→1 (broken, then clear) for one pass | After 2 s the light-curtain monitoring arms (LIGHT_CURTAIN_MONITORING = 1): from now on, breaking the beam again will abort |
| T3 | STATUS-HUTCH_ENTERED → STATUS-ASB1 | Press `ASB-01`, deep inside the hutch | ASB-01 press (0→1) | STATUS-ASB1 = 1; ASB-01 LED on |
| T4 | STATUS-ASB1 → STATUS-ASB2 | Press `ASB-02` | ASB-02 press (0→1) | STATUS-ASB2 = 1; ASB-02 LED on |
| T5 | STATUS-ASB2 → STATUS-ASB3 | Press `ASB-03` | ASB-03 press (0→1) | STATUS-ASB3 = 1; ASB-03 LED on |
| T6 | STATUS-ASB3 → STATUS-ASB4 | Press `ASB-04` | ASB-04 press (0→1) | STATUS-ASB4 = 1; ASB-04 LED on; light-curtain monitoring ends (LIGHT_CURTAIN_MONITORING = 0) |
| T7 | STATUS-ASB4 → STATUS-STANDBY | Press the final button `ASBF-01` by the exit door, then leave and shut the door | All general doors and the gate closed (2-out-of-3 healthy, SIF-06, the search-complete proof) | General doors and gate lock; STANDBY sign on; blue lights on; speaker SP02 says "radiation imminent"; beam-off indicators on; the 180 s beam-delay starts; KEY-01 is released |
| T8 | STATUS-STANDBY → STATUS-BEAM_ON | The operator requests beam enable | The 180 s beam delay has elapsed and all locks are confirmed (SIF-07, the beam-on master permit, is healthy) | BEAM ON sign on; Beam-On indicator on; power contactors energise; the SEARCHED_AND_LOCKED bit latches |
| T9 | STATUS-BEAM_ON → STATUS-OPEN | Press a beam-off button, or the source is confirmed at zero | A beam-off press, or source-off proven (SIF-03, "source is really off, doors may unlock") | The hutch heads back toward OPEN (after a 60 s reset delay) |

__________________________________________________

## 2.4 The two timers that police the search

The PLC uses two independent timing layers. Both must be satisfied.

Overall search timer — `MAX_SEARCH_TIME = 180 s`. The whole walk

(STATUS-START_SEARCH → STATUS-STANDBY) must finish inside 180 seconds,    or it aborts. While it runs, SEARCH_TIMER_RUNNING = 1; if it runs out,    SEARCH_TIME_EXCEEDED = 1.

Per-step window — `5 s … 60 s`. There are six step timers (one per step,

T1-T2 through T6-T7). Each step must take at least 5 s — you cannot rush or    tailgate — and at most 60 s — you cannot dawdle. Going under 5 s sets that    step's ..._TIMER_TRIP_LOW; going over 60 s sets its ..._TIMER_TRIP_HIGH.    Either one aborts the search.

So a valid search is: do each step deliberately (wait ≥ 5 s), keep moving (≤ 60 s per step), and finish the whole thing within 180 s.

__________________________________________________

## 2.5 What aborts a search

Any of these throws the SFC into an *_ABORTED state (you will see ABORT_SEARCH or ABORT_START go 1) and sends the hutch back toward STATUS-OPEN:

a wrong button — pressed out of order;

a step done too fast (< 5 s) or too slow (> 60 s), or the whole search

taking longer than 180 s;

the light curtain (LCRx-01) is broken again while it is being monitored

(during steps T2 … T6);

an enable key (KEY-01 or KEY-02) is lost during the search;

a door opens during the search;

a beam-off button is pressed.

__________________________________________________

## 2.6 Practising this sequence

You practise this exact sequence in HIMA SILworX offline simulation. The per-step minimum is 5 s, so you must let real time pass between presses. The precise tags to force and the signals to watch — step by step, including the abort cases — are written out in document 04 (the SILworX offline test procedure).