# B10E "HeXI" Personnel Safety System

# Logic Study Pack & Simulator Documentation

Diamond Light Source B10E HeXI PSS - SIL 2 - HIMax / HIMA SILworX

# B10E "HeXI" Personnel Safety System — Logic Simulator & Study Pack

A self-contained kit to understand and simulate the safety logic in this repository, written for a junior technical-support engineer. No PLC, no licences and no internet are needed — just Python 3.

What is this system? The three files in the repo describe the Personnel Safety System (PSS) for the Diamond Light Source B10E "HeXI" synchrotron beamline. It is a SIL-2 radiation/personnel-protection interlock running on a HIMax redundant safety PLC (programmed in HIMA *SILworX*). Its job: make it impossible for the X-ray/electron-source/RF hazard to be energised while a person could be inside the shielded "hutch" — and to force the hazard off if anything unsafe happens.

__________________________________________________

## The three source files (and what each one is for)

| File in repo | What it is | Why it matters |
| --- | --- | --- |
| TDI-PSS-B10E-C&E Cause & Effect Matrix (14-04-26) v4.0.pdf | Cause & Effect (C&E) matrix (per BS EN IEC 62881) | The contract: which causes (sensors) drive which effects (outputs), with voting, timing and the SIF they belong to. |
| C15862H-HeXI-IOS.xlsx | I/O Schedule (IOS) | Which physical PLC channel each signal is wired to (AI module 005, DI 007/008/009, DO 013–016). |
| program.pdf | SILworX program printout (713 pages) | The actual PLC code: the 12 SIFs, the search SFC, all timers, latches and voting blocks. |

This kit turns those documents into something you can *run*.

__________________________________________________

## What's in this folder

B10E-PSS-Simulator/
├── README.md                     <- you are here
├── pss_sim.py                    <- the SIMULATOR ENGINE (logic model, heavily commented)
├── pss_cli.py                    <- INTERACTIVE keyboard driver  (python3 pss_cli.py)
├── scenarios.py                  <- 7 worked examples + self-test (python3 scenarios.py)
├── data/
│   ├── cause_effect.json         <- machine-readable C&E (causes, effects, SIFs, voting, timers)
│   ├── io_map.json               <- the full I/O list extracted from the IOS spreadsheet
│   ├── ios_csv/                  <- the IOS spreadsheet exported sheet-by-sheet (readable)
│   └── program_extracted.txt     <- searchable text of all 713 program pages
└── docs/
    ├── 01_SYSTEM_AND_CAUSE_EFFECT.md   <- the big picture + how to read the C&E
    ├── 02_SEARCH_SEQUENCE.md           <- the T1..T7 hutch search, step by step
    ├── 03_TEST_PROCEDURE.md            <- step-by-step functional test for every SIF
    ├── 04_PROGRAM_LOGIC_REFERENCE.md   <- exact PLC logic (SIFs, FBs, timers, latches)
    └── 05_HOW_TO_USE_THE_SIMULATOR.md  <- every command, with examples

__________________________________________________

## Quick start (60 seconds)

cd B10E-PSS-Simulator

# 1) Prove the model matches the Cause & Effect matrix (7 scenarios):
python3 scenarios.py

# 2) Drive it yourself:
python3 pss_cli.py
#   then type:   search        (runs a full valid search and turns BEAM ON)
#                bob 3         (press a beam-off button -> watch everything trip)
#                reset BOB     (clear the latch)
#                door GADC01 open   then   door GADC02 open   (2oo3 door trip)
#                help          (all commands)

Nothing here is connected to real plant. It is a learning model of the logic. Where the simulator simplifies the real PLC, it says so in the comments and in docs/04_PROGRAM_LOGIC_REFERENCE.md.

__________________________________________________

## Where to go next

New to the system? Read docs/01_SYSTEM_AND_CAUSE_EFFECT.md.

Need the test steps? Read docs/03_TEST_PROCEDURE.md and run each one in

the CLI as you go.

Want the exact PLC logic? docs/04_PROGRAM_LOGIC_REFERENCE.md.

# 1 · The system, and how to read the Cause & Effect matrix

*Audience: a junior technical-support engineer who has not seen this system before.*

__________________________________________________

## 1.1 What is being protected, and from what

B10E "HeXI" is a synchrotron beamline. Part of it is a shielded room called a hutch. Inside the hutch there are hazards that can kill or seriously harm a person:

Ionising radiation from the electron source / X-ray beam,

RF (radio-frequency) power,

Oxygen depletion / asphyxiation (cryogenic gases such as liquid nitrogen).

The Personnel Safety System (PSS) is an independent safety PLC whose entire purpose is one idea:

A person and the hazard must never be in the hutch at the same time.

It enforces this two ways:

Before the hazard is turned on, a person must physically **walk through and

"search" the hutch to prove nobody is inside, then lock the doors. This is    the search sequence** (see 02_SEARCH_SEQUENCE.md).

While the hazard is on, if *anything* unsafe happens (a door opens, a

beam-off button is pressed, radiation is detected outside limits, oxygen    drops), the system removes the hazard within milliseconds by de-energising    power contactors.

It is rated SIL 2 (Safety Integrity Level 2 — a measure of how trustworthy the protection must be, from IEC 61508/61511).

__________________________________________________

## 1.2 The two halves of every safety function: CAUSE and EFFECT

Every safety system can be read as a list of:

Causes — the *inputs*: sensors, buttons, switches. A cause is either

healthy or in demand (asking for protection). Examples: a door-closed   switch (demand = door open), a beam-off button (demand = pressed), an oxygen   monitor (demand = O₂ low).

Effects — the *outputs*: the things the PLC switches. Examples: a power

contactor (a big relay that feeds the hazard), a door-lock solenoid, a lamp, a   siren.

The Cause & Effect (C&E) matrix is simply a big grid: causes down the side, effects across the top, and a mark where "this cause makes that effect go to its safe state". This project's C&E follows BS EN IEC 62881.

### Fail-safe / "de-energise to trip"

Almost every effect here is de-energise to trip. That means:

OFF = SAFE. Power contactor *open* (hazard isolated), door solenoid *de-energised* (door unlocked so people can get out), valve *closed*.

So if a wire breaks or the PLC loses power, everything falls to the safe state. In the simulator, an output shown as ON/energised means *the hazard is enabled* or *the door is locked*; off means *safe*.

__________________________________________________

## 1.3 Voting — "how many sensors must agree before we act"

Safety sensors are duplicated so that one faulty sensor cannot (a) cause a dangerous failure, nor (b) cause a nuisance trip. The notation is NooM ("N out of M"): trip when N of the M sensors in the group agree.

| Voting | Meaning | Used here for |
| --- | --- | --- |
| 2oo3 | 2 of 3 must agree to trip — tolerates 1 failed sensor | doors (GADC/SADC), current & voltage transmitters |
| 1oo2 | 1 of 2 trips | service door pair, radiation monitors |
| 1oo4 | any 1 of 4 trips (very sensitive) | oxygen monitors |
| 1oo7/1oo8 | any 1 button trips | beam-off buttons |
| 1oo1 | single channel | enable keys |

The simulator implements all of these in one tiny function — see vote() in pss_sim.py. Try it: in the CLI, ai IT01 12 then ai IT02 12 — one transmitter high does nothing, the second one (2 of 3) declares "radiation present".

__________________________________________________

## 1.4 The causes in this system (the inputs)

Grouped the way the C&E groups them (the letter is the C&E "Group" column):

| Group | Cause tags | What it senses | Voting | Drives |
| --- | --- | --- | --- | --- |
| A | GADC01-03 | General Access Door closed | 2oo3 | SIF-01 |
| B | GADC04-06 | General Access Gate closed | 2oo3 | SIF-13 |
| C | SADC01-03 | Service Access Door closed | 2oo3 | SIF-02/05 |
| D | SADC04-05 | Service Access Door closed (2nd) | 1oo2 | SIF-02/05 |
| E | IT01-03 | Electron-source current present | 2oo3 | SIF-03 |
| F | VT01-03 | Electron-source voltage present | 2oo3 | SIF-03 |
| H | OXMON01-04 | Oxygen depletion | 1oo4 | SIF-11 |
| J | BOB01-08 | Beam-Off Buttons (dual-channel) | 1oo7 | SIF-08 |
| K | RDMN01-02 | Radiation monitors (dose + rate) | 1oo2 | SIF-09 |
| — | KEY01/02/03 | Enable key switches | 1oo1 | SIF-05/10 |
| — | SCR, LCRx, ASB01-04, ASBF | Search devices (card, light-curtain, buttons) | sequence | SIF-04/05/06 |

## 1.5 The effects in this system (the outputs)

| Effect tags | What it is | Safe state |
| --- | --- | --- |
| CON01-05 | Electron-source power contactors | open (isolated) |
| CON06-08 | 3-phase RF power contactors | open |
| CON09-10 | 1-phase RF drive contactors | open |
| GADL01-04, SADL01-02 (SOL-01..06) | Door/gate lock solenoids | unlocked |
| ANNOPN/ANNRES/ANNSTD/ANNBON | Hutch status annunciator sign | off |
| SP01/SP02/SP03 | Speaker/beacon programs (caution/deterrent/alarm) | off |
| BLUEL01-04 (-06) | Blue lights (radiation deterrent) | off |
| BONI / BOBI01-04 | "Beam On" / "Press Beam Off" indicators | off |
| SDVLN2 | Liquid-nitrogen shut-off valve | closed |
| IND01-03 | O₂ / toxic-gas traffic-light indicators | red |

## 1.6 The 12 Safety Instrumented Functions (SIFs)

A SIF is one self-contained protective function. The PLC has 12 (SIF-01…11 and SIF-13 — there is no SIF-12 in the PLC; the C&E lists the oxygen function as "SIF 11 & 12"). One-line summary of each:

| SIF | Protects against | Cause → Effect |
| --- | --- | --- |
| 01 | someone opening the general door with beam on | GADC 2oo3 → drop CON01-03 |
| 02 | someone opening the service door | SADC 2oo3/1oo2 → drop CON01-03 |
| 03 | unlocking doors while radiation still present | IT/VT 2oo3 → keep locks ON until source reads 0 for 20 s + Open/Reset |
| 04 | the search itself (the SFC state machine) | sequence → status flags |
| 05 | starting a search without authority | card + keys + doors → permit T1 |
| 06 | declaring "searched" with a door open | GADC + gate 2oo3 → permit T7 |
| 07 | turning beam on before locks confirmed | lock feedback + 180 s → beam permit |
| 08 | emergency stop — any beam-off button | BOB 1oo7 → drop CON01-03,06-10 |
| 09 | radiation detected high | RDMN 1oo2 → drop CON01-03,09 |
| 10 | RF enabled without the enable key | KEY03 → drop CON06-10 |
| 11 | oxygen depletion | OXMON 1oo4 → close LN2 valve, alarm |
| 13 | someone opening the gate | GADC gate 2oo3 → drop CON06-08 (200 ms) |

The exact gate logic, latching and timers are in 04_PROGRAM_LOGIC_REFERENCE.md.

__________________________________________________

### Try it now

python3 pss_cli.py
pss> ai OXMON02 18        # one oxygen monitor reads 18% (< 19.5 trip)  -> SIF-11
pss> state                # LN2 valve CLOSES, O2 lights go RED
pss> reset GAS            # clear it (after O2 restored)

# 2 · The hutch SEARCH sequence (T1 → T7 → Beam On)

*This is the heart of the system. It is SIF-04, implemented in the PLC as a Sequential Function Chart (SFC). Read this, then drive it in the simulator.*

__________________________________________________

## 2.1 Why a "search"

Before the radiation/RF hazard can be switched on, a trained person must physically walk through the whole hutch to confirm nobody is left inside, in a fixed order, within strict time windows, and then lock the doors behind them. The PLC only lets the beam on if that exact ritual is completed correctly. If the searcher does anything wrong — wrong button, too fast, too slow, or a door opens — the search aborts and they must start again.

This defends against the worst case: a person hiding/working in the hutch while a colleague switches the beam on.

__________________________________________________

## 2.2 The states (what the hutch is doing)

These are the real PLC state names (STATUS-* flags), confirmed from program.pdf:

OPEN ──▶ OPEN_READY ──▶ START_SEARCH ──▶ HUTCH_ENTERED ──▶ ASB1 ──▶ ASB2
                            (T1)              (T2)           (T3)     (T4)
                                                                       │
        OPEN ◀── BEAM_ON ◀── STANDBY ◀── ASB4 ◀── ASB3 ◀──────────────┘
        (T9)      (T8)         (T7)       (T6)     (T5)

| State | Meaning | Annunciator sign |
| --- | --- | --- |
| OPEN | doors unlocked, anyone may enter, no hazard | OPEN |
| OPEN_READY | all doors closed & keys in — ready to start | OPEN |
| START_SEARCH | search begun; service doors lock | RESTRICTED |
| HUTCH_ENTERED | searcher passed the light curtain | RESTRICTED |
| ASB1..ASB4 | area-search buttons pressed in order | RESTRICTED |
| STANDBY | search done, all doors locked, 180 s warning dwell | STANDBY |
| BEAM_ON | hazard enabled | BEAM ON |

__________________________________________________

## 2.3 The steps, one at a time

Each transition Tn is "the event that moves you to the next state".

| T | From → To | What the searcher does | PLC pre-condition | What happens on arrival |
| --- | --- | --- | --- | --- |
| T1 | OPEN_READY → START_SEARCH | Insert search card (SCR) and turn KEY01 (electron-source) and KEY02 (hutch) to ON | service doors closed (SADC), no beam-off latched (SIF-05) | Service doors lock; RESTRICTED sign; Speaker SP01 "search in progress"; white lights on; 180 s search timer starts |
| T2 | START_SEARCH → HUTCH_ENTERED | Walk through the light curtain once (single pass) | — | Light-curtain monitoring arms after 2 s |
| T3 | HUTCH_ENTERED → ASB1 | Press ASB-01 (deep in the hutch) | light curtain monitored | ASB-01 LED on |
| T4 | ASB1 → ASB2 | Press ASB-02 | light curtain monitored | ASB-02 LED on |
| T5 | ASB2 → ASB3 | Press ASB-03 | light curtain monitored | ASB-03 LED on |
| T6 | ASB3 → ASB4 | Press ASB-04 | — | ASB-04 LED on; light-curtain monitoring ends |
| T7 | ASB4 → STANDBY | Press the final button ASBF by the door | all general doors & gate closed (2oo3, SIF-06) | General doors/gate lock; STANDBY sign; blue light on; Speaker SP02 "radiation imminent"; beam-off indicators on; 180 s beam-delay starts; KEY01 released |
| T8 | STANDBY → BEAM_ON | (operator enables beam) | 180 s elapsed and all locks confirmed (SIF-07) | BEAM ON sign; Beam-On indicator; contactors energise; latch SEARCHED_AND_LOCKED |
| T9 | BEAM_ON → OPEN | press a beam-off button, or source confirmed zero (SIF-03) | — | returns toward OPEN (60 s reset delay) |

__________________________________________________

## 2.4 The two timers that police the search

The PLC uses two independent timing systems (both verified in program.pdf):

Overall search timer — `MAX_SEARCH_TIME = 180 s`. The whole walk

(START_SEARCH → STANDBY) must finish inside 180 seconds, or it aborts.

Per-step window — `5 s … 60 s` (six `Transition_Timer` blocks). Each step

must take at least 5 s (you cannot rush / tailgate) and at most 60 s    (you cannot dawdle). Outside that → abort.

So a valid search is: do each step *deliberately* (wait ≥5 s), keep moving (≤60 s/step), and finish the lot within 180 s.

__________________________________________________

## 2.5 What aborts a search

Any of these throws the SFC into an *_ABORTED state and back toward OPEN:

a wrong button (out of order),

a step done too fast (<5 s) or too slow (>60 s), or the whole search >180 s,

the light curtain is interrupted again while it is being monitored (T2…T6),

an enable key (KEY01/KEY02) is lost during the search,

a door opens during the search,

a beam-off button is pressed.

__________________________________________________

## 2.6 Drive it in the simulator

The per-step minimum is 5 s, so you must let time pass between presses. The CLI search macro does this for you; or do it by hand to *feel* the timing:

python3 pss_cli.py

pss> card            # T1: insert card (keys are already IN). -> START_SEARCH, RESTRICTED
pss> wait 10         # let 10 s pass (>=5, <=60)
pss> lcrx            # T2 -> HUTCH_ENTERED
pss> wait 10
pss> asb1            # T3 -> ASB1
pss> wait 10
pss> asb2            # T4
pss> wait 10
pss> asb3            # T5
pss> wait 10
pss> asb4            # T6
pss> wait 10
pss> asbf            # T7 -> STANDBY (doors lock, blue light, 'radiation imminent')
pss> enable          # operator beam-enable request
pss> wait 180        # the 180 s 'radiation imminent' dwell
pss> state           # -> BEAM_ON: contactors energised, BEAM ON sign

Now try breaking it:

pss> card
pss> wait 2          # only 2 s ...
pss> lcrx            # ... too fast -> ABORT (read the 'last abort' line)

pss> card
pss> wait 10
pss> asb1            # wrong! light curtain (lcrx) expected first -> ABORT

# 3 · Test procedure — every step

*A functional-test walkthrough of the B10E PSS, written so a junior engineer can follow it exactly. Each test states: purpose → setup → action → expected result, and gives the simulator commands so you can rehearse it before ever touching real plant.*

Two kinds of "test" — don't mix them up * Functional / proof test (this document): prove each Safety Function does   what the Cause & Effect matrix says (right cause → right effect). That is what   the simulator reproduces. * Hardware service test: measuring 24 V/5 V rails, checking crimps, fans,   earth, module seating, etc. That is a *separate*, generic HIMA field-service   checklist and is not part of this project's logic. (An old generic copy of   that form was in the repo's history and has been removed.)

Golden rule for real plant: only do these on a system that has been formally taken out of service / under a permit to work, with the beam interlock isolated as your site procedure requires. Tripping a live safety function on a running machine is never a "quick check".

__________________________________________________

## 3.0 Before you start (every test)

Record the starting state: in the simulator type state; on real plant, read

and save the diagnostic/event list first (before you touch anything).

Confirm the healthy baseline: all doors closed, keys IN, no latched trips,

annunciator OPEN/OPEN_READY.    ``    python3 pss_cli.py    pss> state          # expect HUTCH STATE: OPEN_READY, all contactors off (safe), no TRIPS

Know your reset: each latched function has its own reset button

(reset BOB, reset RDMN, reset GAS, reset OR).

__________________________________________________

## TEST 1 — SIF-08 Beam-Off Buttons (1oo7 emergency stop)

Purpose: any single beam-off button must remove the beam, and the trip must latch until reset.

Setup: get to BEAM_ON.

pss> search                 # macro: full valid search + beam enable -> BEAM_ON
pss> state                  # confirm: CON01-05 ON, annunciator BEAM ON

Action & expected result:

| Step | Action | Expected |
| --- | --- | --- |
| 1 | bob 3 (press beam-off button 3) | all electron-source CON01-05 and RF CON06-10 go off; state leaves BEAM_ON; TRIPS: SIF-08 ... (latched) |
| 2 | bob 3 up (release the button) | contactors stay off (latched) — releasing does not restart the hazard |
| 3 | reset BOB | latch clears (latch=off) |
| 4 | repeat for buttons 1–8 | each one alone must trip (1oo7) |

Why it matters: this is the operator's emergency stop; it must work from any one of the 8 stations and must never auto-restart.

__________________________________________________

## TEST 2 — SIF-01 General Access Door (2oo3)

Purpose: opening the general door with beam on isolates the source; and prove the 2oo3 voting (1 switch alone must NOT trip — that would be a nuisance trip).

Setup: search → BEAM_ON.

| Step | Action | Expected |
| --- | --- | --- |
| 1 | door GADC01 open | no trip — only 1 of 3 switches (2oo3 tolerates one) |
| 2 | door GADC02 open | now 2 of 3 → CON01-03 off, drops out of BEAM_ON, SEARCHED_AND_LOCKED latch broken |
| 3 | door GADC01 close + door GADC02 close | doors closed again, but beam does not come back — you must run a new search |
| 4 | search | beam returns only after a fresh, valid search |

Real-plant note: the 2oo3 means one failed/disconnected door switch will not shut the beamline down on its own (availability) — but two will (safety).

__________________________________________________

## TEST 3 — SIF-13 General Access Gate (2oo3, 200 ms)

Purpose: the gate is split from the door (Rev 4 of the C&E) and drops the RF contactors CON06-08 with a 200 ms delay.

Setup: search → BEAM_ON.

| Step | Action | Expected |
| --- | --- | --- |
| 1 | door GADC04 open | 1 of 3 gate switches — no trip |
| 2 | door GADC05 open | 2oo3 gate → CON06-08 off (RF power) |

__________________________________________________

## TEST 4 — SIF-02 Service Access Door (2oo3 + 1oo2)

Setup: search → BEAM_ON.

| Step | Action | Expected |
| --- | --- | --- |
| 1 | door SADC01 open then door SADC02 open | group C 2oo3 → source contactors off |
| 2 | reset by closing + new search; then door SADC04 open | group D is 1oo2 — this single one trips |

__________________________________________________

## TEST 5 — SIF-09 Radiation Monitors (1oo2, latched)

Purpose: a high radiation reading removes the hazard and latches.

Setup: search → BEAM_ON.

| Step | Action | Expected |
| --- | --- | --- |
| 1 | bob … no — use the radiation monitor: open the CLI and set demand via state; in this build use the door/analog commands. For RDMN, use the scenario or python3 -c snippet below. | — |

Run it directly:

python3 -c "from pss_sim import *; p=PSS();
import scenarios as s; s.do_full_search(p);
p.demand['RDMN01']=True; p.scan();
print('CON01 =', p.outputs()['CON01'], '(expect False)');
print('latched =', p.latch_rdmn, '(expect True)')"

Expected: CON01 = False, latched = True. Clear with reset RDMN (after the monitor returns to normal). 1oo2: either monitor alone trips.

__________________________________________________

## TEST 6 — SIF-11 Oxygen Depletion (1oo4)

Purpose: any one oxygen monitor reading low closes the LN₂ valve and raises the O₂ alarm.

Setup: any state (this function is independent of the search).

| Step | Action | Expected |
| --- | --- | --- |
| 1 | ai OXMON02 18 (monitor 2 reads 18 % O₂, below 19.5 %) | LN2 valve CLOSES (SDVLN2 off); O₂ traffic-lights RED; alarm beacon |
| 2 | ai OXMON02 20.9 (restore) then reset GAS | valve re-opens, lights green |
| 3 | try each of OXMON01–04 | any one alone trips (1oo4) |

__________________________________________________

## TEST 7 — SIF-03 Radiation-present door interlock (2oo3, 20 s, Open/Reset)

Purpose: you must not be able to unlock the doors while the source is still energised; and even after it reads zero there is a 20 s confirm and an Open/Reset button press before doors release.

| Step | Action | Expected |
| --- | --- | --- |
| 1 | ai IT01 12 then ai IT02 12 | 2oo3 current "present" → radiation_present = YES; door locks held ON |
| 2 | ai IT01 3 ai IT02 3 (back to ~0) then wait 5 | Open/Reset LED still off (only 5 s of the 20 s confirm) |
| 3 | wait 20 | Open/Reset LED comes ON (source confirmed zero for ≥20 s) |
| 4 | reset OR | doors may now unlock; hutch returns toward OPEN |

__________________________________________________

## TEST 8 — SIF-10 Electron-Source Enable Key

| Step | Action | Expected |
| --- | --- | --- |
| 1 | search → BEAM_ON | RF contactors CON06-10 ON |
| 2 | key KEY03 off | SIF-10 → RF/source isolation (key_off trip) |
| 3 | key KEY03 on | does not auto-restart — a key is not a reset; run a new search |

__________________________________________________

## TEST 9 — The SEARCH itself (SIF-04/05/06)

This is Test of the sequence and its interlocks. Work through 02_SEARCH_SEQUENCE.md §2.6. Specifically prove each abort:

| Case | How to provoke | Expected |
| --- | --- | --- |
| Wrong order | card, wait 10, asb1 (before lcrx) | ABORT "out-of-order" |
| Too fast | card, wait 2, lcrx | ABORT "too fast (<5s)" |
| Too slow | card, wait 70, lcrx | ABORT "too slow (>60s)" |
| Door during search | card, wait 10, lcrx, door GADC01 open… GADC02 | ABORT "door opened/hazard during search" |
| Can't declare searched with door open | run to ASB4, door GADC01 open+GADC02, asbf | ASBF refused / aborts (SIF-06 not satisfied) |

__________________________________________________

## 3.x Test record template

For each test, record:

SIF / Test no.: ____    Date: ____    Engineer: ____
Pre-state recorded?  Y / N
Cause applied:        ___________________________
Expected effect:      ___________________________
Observed effect:      ___________________________
Latched? reset OK?    Y / N
PASS / FAIL:          ____      Notes: __________

Run the whole functional set automatically at any time with:

python3 scenarios.py     # 7 scenarios, PASS/FAIL each, must be 7/7

# 4 · Program logic reference (the exact PLC code)

*This is the authoritative map of program.pdf (713 pages, HIMA SILworX export, SILworX v16, project C15862H-BL10E, configuration BL10E_HeXI [400], target HIMax, SIL 2). The searchable text is in data/program_extracted.txt (page markers ===== PAGE n =====).*

Convention in SILworX FBD text: & = AND, >=1 = OR, NOT/a bubble = invert. All effects are de-energise-to-trip: an output FALSE = tripped/safe; a SIF ..._OUTPUT/..._TRIP signal TRUE usually means healthy/permissive.

__________________________________________________

## 4.1 Page index (where everything lives)

| Pages | Area |
| --- | --- |
| 1–13 | Cover + Table of Contents |
| 14–16 | Project structure (POU tree, lists all SIFs) |
| 37–126 | Global Variables & cross-references (the master tag list + initial values, setpoints, timer presets) |
| 127–149 | Hardware (HIMax I/O module config) |
| 151–285 | C15862H_Lib — custom application logic (see 4.4) |
| 286–382 | The 12 SIFs (core safety logic) |
| 383–690 | X_Lib — HIMA standard blocks (voters, timers, limits) |
| 691–710 | Modbus TCP / OPC-UA / safeethernet |
| 711–713 | Watchpages (Global Forcing) |

## 4.2 The 12 SIFs (page → logic)

| SIF | Pages | Logic pg | Title |
| --- | --- | --- | --- |
| SIF-01 | 287–291 | 291 | General Access Door Closed |
| SIF-02 | 292–297 | 297 | Service Access Door Closed |
| SIF-03 | 298–303 | 303 | Current & Voltage Monitoring |
| SIF-04 | 304–338 | 326–338 | Search Sequence (SFC) |
| SIF-05 | 339–344 | 344 | Search Start |
| SIF-06 | 345–350 | 350 | Search Complete |
| SIF-07 | 351–356 | 356 | Beam On (permissive) / lock feedback |
| SIF-08 | 357–363 | 363 | Beam Off Buttons |
| SIF-09 | 364–368 | 368 | Radiation Monitoring |
| SIF-10 | 369–372 | 372 | Electron Source Enable |
| SIF-11 | 373–377 | 377 | Oxygen Monitoring |
| SIF-13 | 378–382 | 382 | General Access Gate Closed |

*(No SIF-12 in the PLC — the C&E "SIF 11 & 12" both refer to the oxygen function.)*

## 4.3 Per-SIF logic (plain English)

SIF-01 (p.291) — GADC-01/02/03 voted 2oo3 (X_2oo3_B), AND'd with

SIF-07_OUTPUT (beam-on conditions). Output SIF-01_TRIP → contactors   CON-01/02/03 via the central Logic POU.

SIF-02 (p.297) — SADC-01/02/03 2oo3 OR SADC-04/05 (1oo2 pair),

AND'd with SIF-07_OUTPUT. Outputs SIF-02_TRIP, SERVICE_DOOR_CLOSED.

SIF-03 (p.303) — "is the beam actually off?" + door-unlock permit.

Current IT-01/02/03 2oo3 and Voltage VT-01/02/03 2oo3. An RS latch + a   TON DOOR_UNLOCK_DELAY = T#20s + R_TRIG on Open/Reset pushbutton   OR-01 and key KEY-01: the Open/Reset button only becomes live once both   2oo3 votes read zero for ≥20 s, then OR-01:LED lights. (The C&E footnote   mentions 12 s from the SRS; the implemented value is 20 s.)

SIF-04 (pp.326–338) — the SFC (see 4.5).

SIF-05 (p.344) — Search-start permit (T1): SCR-01 card AND KEY-01

AND KEY-02 AND service-door 2oo3 AND 1oo2 pair AND SIF-08 healthy →   SIF-05_START.

SIF-06 (p.350) — Search-complete: general door 2oo3 AND gate 2oo3 →

SIF-06_TRIP (the T7 proof that all doors are shut).

SIF-07 (p.356) — master beam-on permissive: door-lock confirmation

switches GADL-01/02/04/05 + SADL-01/02 + SIF-06, with a TON   BEAM_DELAY_TIMER = T#180s and an RS latch → SIF-07_OUTPUT. Consumed by   SIF-01/02/13 and the SFC.

SIF-08 (p.363) — eight dual-channel beam-off buttons BOB-01…08

(:A/:B AND'd per button), 1oo7 (any one), RS-latched, reset   IOC-01-BOB:RESET. Drops CON-01,02,03,06,07,08,09,10 and instantly unlocks.

SIF-09 (p.368) — RDMND-01/02 (dose) + RDMNR-01/02 (rate), 1oo2,

RS-latched, reset IOC-01-RDMN:RESET. Drops CON-01/02/03 and CON-09.

SIF-10 (p.372) — KEY-03 rack key (1oo1) → SIF-10_TRIP; gates CON-04/05

(and CON-09/10 RF). Combined with KEY-01 (ZCP) elsewhere.

SIF-11 (p.377) — OXMON-01…04, 1oo4, RS-latched, reset

IOC-01-GAS:RESET. Closes LN₂ valve SDVLN2, switches O₂ beacons/indicators   IND-01/02/03 and speaker SP02.

SIF-13 (p.382) — gate GADC-04/05/06 2oo3, AND'd with SIF-07_OUTPUT →

drives CON-06/07/08 with a 200 ms delay. (Added in Rev 4.0 to split gate   from door.)

## 4.4 The central `Logic` POU (pp.267–269) — cause → effect

This is the block that actually drives the outputs:

Contactors (p.267): combine the SIF trips per group and RS-latch them so

that CON-01,02,03,06,07,08,09,10 cannot re-energise after a trip without a   fresh full search (the SEARCHED_AND_LOCKED latch). This is why, in the   simulator, you must re-search after any door/BOB trip.

Door/gate solenoids `SOL-01…06`: service doors lock when the search

*starts*; general doors/gate lock when the *final* button is pressed; all   unlock when status = Open or SIF-08 is active.

Lights/annunciators/sounders (pp.268–269): white light vs blue light

interlock, annunciator OPEN/RESTRICTED/STANDBY/BEAM-ON, key solenoids, speaker   programs, O₂ beacon.

## 4.5 The Search SFC + Transition_Timer (SIF-04)

Layer 1 — the SFC steps (Modbus bit in brackets): Open (0) → Open-Ready (1) → Search_Start (2) → Hutch_Entered (3) → ASB1 (4) → ASB2 (5) → ASB3 (6) → ASB4 (7) → Standby (8) → Beam On (9); with abort branches Search_Aborted, Start_Aborted, Run_Aborted. (Modbus bit 10 = SEARCHED_AND_LOCKED — a convenient state handle for an HMI.)

Layer 2 — six `Transition_Timer` instances (FB defined p.285), one per gap T1-T2 … T6-T7. Each takes Start_Timer, Min_Time, Max_Time, Reset and outputs Below_Min_Time (→ _TRIP_LOW), Exceed_Max_Time (→ _TRIP_HIGH) and Transition_Time (ms). All six use `Min = T#5s`, `Max = T#60s` and are reset by STATUS-START_SEARCH.

## 4.6 Verified timing constants (Global Variables)

| Tag | Value | Purpose |
| --- | --- | --- |
| MAX_SEARCH_TIME | 180 s | overall search watchdog |
| T1-T2…T6-T7_TIMER_MIN | 5 s | min per-step time (faster ⇒ abort) |
| T1-T2…T6-T7_TIMER_MAX | 60 s | max per-step time (slower ⇒ abort) |
| BEAM_DELAY_TIMER_TIME | 180 s | Standby → Beam-On dwell |
| RESET_DELAY_TIMER | 60 s | delay returning to Open |
| DOOR_UNLOCK_DELAY | 20 s | SIF-03 zero-source confirm |
| LIGHT_CURTAIN_DELAY | 2 s | LC monitoring arm delay |
| gate/RF contactor delay | 200 ms | CON-06…10 trip delay |

## 4.7 Function-block types used

Voters: X_2oo3_B (sum of 3 BOOLs ≥ 2; also a discrepancy Dev output) —

used in SIF-01/02/03/05/06/13. The higher votes 1oo4/1oo7/1oo2 in SIF-08/09/11   are done with plain &/>=1 gating + RS latches, not voter blocks.

Analogue trips: X_LimH (high trip) and X_LimL (low trip), each with

hysteresis, trip-delay DT, Inhibit, Reset, Ch_ok. X_Hx_AI scales raw   HIMax counts to engineering units.

IEC blocks: TON (on-delay), TP (pulse), RS/SR (latches),

R_TRIG/F_TRIG (edge detect), MOVE, LIMIT, comparators.

Custom: Transition_Timer, 2In_/3In_Discrepency_Alarm.

## 4.8 Analogue setpoints (as exported)

| Signal | Block | Setpoint | Hyst |
| --- | --- | --- | --- |
| OXMON-01…04 (O₂) | X_LimL (low) | 25.0 (full-scale placeholder; commissioned value ≈ 19.5 %) | 0.2 |
| IT-01…03 (current) | X_LimH (high) | 0.0 (placeholder) | 0.2 |
| VT-01…03 (voltage) | X_LimH (high) | 0.0 (placeholder) | 0.2 |
| RDMN dose/rate | digital trip contacts (>4 mA per C&E) | — | — |

Each AI channel also exposes _OC (open-circuit), _SC (short-circuit) and _CH_OK diagnostics. The simulator uses 19.5 %O₂ and 4 mA as illustrative trip points — adjust in data/cause_effect.json to match the commissioned values.

## 4.9 Things worth knowing for support work

Latching / "no silent restart": trips and the search-complete state are RS

latches. After any trip you need an explicit reset *and* (for the hazard) a   fresh search. Modelled exactly in the simulator.

Resets are separate: IOC-01-BOB:RESET (SIF-08), …-RDMN:RESET (SIF-09),

…-GAS:RESET (SIF-11), Open/Reset OR-01 (SIF-03, only live after the 20 s   zero-source confirm — watch OR-01:LED).

Dual-channel devices (BOB, BLUEL, ANNUN, BONI, BOBI) are read as :A/:B

pairs and AND'd; discrepancy-alarm blocks give first-up annunciation.

No application bypass/maintenance-override block exists — overrides are done

only via SILworX Global Forcing (Watchpages pp.711–712). (If you saw an   LXS_BYPASS block elsewhere, that belongs to a *different, unrelated* project   that used to be in this repo's history — not B10E.)

Comms: Modbus TCP slave on port 502 exposes the SFC state bits and the

oxygen readings; an OPC-UA server mirrors most tags. Good HMI/SCADA handles.

Naming wart: the PLC tag database uses BL10E-PS-… while the SIF block

names and the C&E "EPICS/DCS Tag" use B10E-PS-…. Same devices. Door locks   appear twice: as outputs SOL-01…06 and as feedback inputs GADL-/SADL-.

*External drawings referenced by the C&E but not in this repo:* SRS TDI-PSS-SRS-0002, SIF logic Dwg 1224211, layout Dwg 1212854.

# 5 · How to use the simulator

*No installation. Pure Python 3 standard library. Nothing connects to real plant.*

__________________________________________________

## 5.1 The three programs

| Command | What it does |
| --- | --- |
| python3 scenarios.py | Runs 7 worked examples as a self-test (PASS/FAIL). Run this first — if it is 7/7, the model matches the Cause & Effect matrix. |
| python3 pss_cli.py | Interactive — you type commands, it shows the live state. This is the one you'll use to learn and to rehearse the test procedure. |
| pss_sim.py | The engine (imported by the other two). Read it to see the logic in ~350 commented lines. |

## 5.2 Reading the status panel

After every command the CLI prints a panel. Top line = HUTCH STATE (the SFC step) with the search/step timers. Then:

inputs: card, keys, beam request; the open-vote counts for each door group

(e.g. Gen DOOR (grp A 2oo3) open-votes 1/3); current/voltage votes →   radiation_present; oxygen/BOB/RDMN counts and latch state.

outputs (ON = energised): e-source contactors C01..C05, RF C06..C10,

door locks, annunciator sign, blue lights/indicators, beacons, LN₂ valve, O₂   lights, and the Open/Reset LED.

Remember ON = energised: for a contactor that means *hazard powered*; for a lock it means *door locked*; lowercase/off = the safe state.

If something has tripped, a red TRIPS: line lists the reasons. If a search was aborted, a yellow last abort: line tells you why.

## 5.3 Command reference

| Command | Example | Meaning |  |
| --- | --- | --- | --- |
| search | search | auto-run a full valid search → BEAM_ON (does the waits for you) |  |
| card / start | card | insert the search card (begins T1 if keys/doors OK) |  |
| lcrx | lcrx | light-curtain single pass-through (T2) |  |
| asb1…asb4 | asb1 | press an area-search button (T3…T6) |  |
| asbf | asbf | final search button (T7 → STANDBY) |  |
| enable | enable | operator "enable beam" request (needed for T8) |  |
| wait <s> | wait 10 | let time pass — needed between search steps (≥5 s) |  |
| `door <tag> open\ | close` | door GADC01 open | move a door switch (GADC01-06, SADC01-05) |
| bob <n> [up] | bob 3 / bob 3 up | press/release beam-off button n (1-8) |  |
| `key <K> on\ | off` | key KEY03 off | turn an enable key (KEY01/02/03) |
| ai <tag> <val> | ai OXMON02 18 | set an analogue input (OXMON01-04, IT01-03, VT01-03) |  |
| lc | lc | extra light-curtain interrupt (aborts a monitored search) |  |
| reset <R> | reset BOB | press a reset PB (BOB / RDMN / GAS / OR) |  |
| state | state | reprint the panel |  |
| log | log | last 15 internal events (advances/aborts) |  |
| help / quit |  | help / exit |  |

## 5.4 Five things to try (10 minutes)

Happy path: search → watch it reach BEAM_ON with contactors energised.

E-stop & latch: from BEAM_ON, bob 1 (everything trips), bob 1 up

(stays tripped), reset BOB, then search again to recover.

2oo3 voting: from BEAM_ON, door GADC01 open (no trip), `door GADC02

open` (trips). One switch is tolerated, two are not.

Oxygen: ai OXMON03 17 → LN₂ valve closes, O₂ lights red; `ai OXMON03

20.9 + reset GAS` to clear.

Break a search: card, wait 2, lcrx → aborts "too fast"; or card,

wait 10, asb1 → aborts "out-of-order".

## 5.5 Changing the data

Everything the engine knows lives in data/cause_effect.json:

setpoints (e.g. oxygen 19.5 %, current/voltage 4 mA),

voting schemes per group,

the timing constants,

which causes/effects belong to which SIF.

Edit that file and re-run scenarios.py — no code change needed for setpoints or voting. The exact PLC values are in docs/04_PROGRAM_LOGIC_REFERENCE.md §4.6/4.8.

## 5.6 Honest limits of the model (so you don't over-trust it)

This is a teaching model of the logic, not the certified PLC code. In particular:

It is a clean state-machine; the real PLC also runs diagnostics, channel

OC/SC fault handling, discrepancy alarms, and dual-CPU voting that are not   modelled here.

Analogue behaviour is a simple setpoint compare (no scaling curve / hysteresis

detail).

The light-curtain "single pass vs re-interrupt" and the per-step 5–60 s windows

are modelled in spirit; confirm exact edge-cases against program.pdf.

Timing is event-driven via wait/tick, not real-time.

For anything that affects real plant, the C&E matrix, the SRS and `program.pdf` are the authority — this simulator is for understanding and rehearsal.

# 6 · SILworX offline-simulation test procedure — v2.2 (complete, with concepts)

*Run this in HIMA SILworX offline simulation against the actual B10E program. For every set of logic it gives you: the Concept (what it protects and why), the Logic as built (the real blocks/signals on the named page), the Test (exact forces and expected observations), and What it proves. Follow it top to bottom and you will have exercised — and understood — the whole program.*

Source of truth: program.pdf (project C15862H-BL10E, configuration BL10E_HeXI [400], SILworX v16.0.0 R3326). Page text: data/program_extracted.txt. Changes from v1: added SIF-05 negative tests, a standalone SIF-07 test, the lock-feedback forcing step (without it the search stalls at STANDBY in offline sim), voltage (VT) tests, verified contactor groupings from p.267, dual-channel discrepancy tests, the KEY-01 release test, and a coverage matrix. v2.1: corrected analogue handling — the _SP setpoints are fail-safe constants (OXMON 25.0 / IT,VT 0.0) that cannot be forced; baseline and SIF-03/-11 tests now force the _TRIP flags (Option A) or require a setpoint edit + code regen (Option B). v2.2: added a plain-language "what the tag is" column to the §0.3 polarity table, and a high-school-level explanation of every timer in §0.5.

__________________________________________________

## 0 · Setup & conventions (read once, it saves hours)

### 0.1 Start offline simulation

Open the project; select Resource `BL10E_HeXI [400]`.

Generate code, then start Offline Simulation on the resource.

Open any logic page (e.g. Library/SIF/B10E-SIF-01) — wires show live values.

Open the Force Editor / a Watch page; add the tags listed in each test.

### 0.2 Concept: forcing replaces the field

In offline simulation there is no I/O. The global variables that normally come from field wiring (BL10E-PS-…) just sit at their initial values — you are the field. Forcing an input variable is "operating the plant". Two traps:

Feedback inputs do not follow outputs. When the program energises a door

lock output (SOL-01), the lock position feedback input (GADL-01) does   NOT change by itself — in the real plant the mechanism moves the switch; in   simulation you must force the feedback to simulate the mechanism. This   matters at T7 (§3) — if you don't force GADL/SADL TRUE after the locks   energise, BL10E-SIF-07_OUTPUT never comes TRUE and beam-on never happens.   The same idea applies to contactor feedbacks (CON-0x:FB) used by the alarm   layer.

Polarity. This program is de-energise-to-trip throughout, so for most

inputs the demand (unsafe) value is 0, and many …_TRIP/…_OUTPUT   signals are permissives: TRUE = healthy, FALSE = tripped. Exception: the   analogue …_TRIP flags (IT/VT/OXMON) are detections: TRUE = limit exceeded.

### 0.3 Polarity table (force the right way)

| Signal | What the tag is (the device and its job) | Healthy / normal | Demand (unsafe / action) |
| --- | --- | --- | --- |
| BL10E-PS-GADC-01..06, SADC-01..05 (door closed sw.) | Position switches on each personnel door and gate — they tell the PLC whether the door is physically shut | 1 = closed | 0 = open |
| BL10E-PS-GADL-01/02/04/05, SADL-01/02 (lock feedback) | Switches on the lock bolts — they confirm a door is *actually* locked, not just that the PLC asked for it | 1 = locked-confirmed | 0 = not locked |
| BL10E-PS-KEY-01/02/03 (enable keys) | Physical key-switches the responsible person turns to allow a search / let the source be energised | 1 = on | 0 = off |
| BL10E-PS-SCR-01 (search card) | Card reader at the door — presenting a valid search card is what starts the search | 1 = card in | 0 = out |
| BL10E-PS-BOB-01..08 :A and :B (beam-off, dual ch.) | Emergency "beam-off" buttons in and around the hutch; each has two separate wired channels (:A, :B) for safety | 1 = not pressed | 0 = pressed |
| BL10E-PS-ASB-01..04, ASBF-01 (search buttons) | Area-search pushbuttons pressed in a set order during the walk-through; ASBF is the final one by the exit door | 0 = idle | pulse 0→1 = press |
| BL10E-PS-LCRx-01 (light curtain) | An invisible infra-red "curtain" across the entrance that detects a person stepping through | 1 = clear | 0 = interrupted |
| BL10E-PS-OR-01 (Open/Reset PB) | The "Open / Reset" button the operator presses to unlock the doors and reset the system once the source is proven off | 0 = idle | pulse 0→1 |
| BL10E-PS-IT/VT-0x_TRIP (BOOL — see §0.4!) | Trip flags from the electron-source current (IT) and voltage (VT) transmitters; 1 means the source is electrically live | force 0 = source dead | force 1 = current/voltage present |
| BL10E-PS-OXMON-0x_TRIP (BOOL — see §0.4!) | Trip flags from the four hutch oxygen monitors; 1 means oxygen has dropped too low (suffocation risk) | force 0 = O₂ healthy | force 1 = O₂ low |
| BL10E-PS-RDMND/RDMNR-01/02 (radiation) | The two radiation monitors: accumulated dose (RDMND) and dose rate (RDMNR) | healthy | trip value → SIF-09 |
| BL10E-PS-IOC-01-BOB/RDMN/GAS/SYS:RESET | Control-room reset buttons — one each for the beam-off, radiation, gas and system latches | 0 | pulse 0→1 = reset |
| OUTPUT BL10E-PS-CON-0x:EN | The PLC's command to a power-contactor coil that feeds the electron source / RF — i.e. switches the hazard ON | — | 1 = energised (hazard live), 0 = safe |
| OUTPUT BL10E-PS-SOL-01..06 (locks) | The PLC's command to a door/gate lock solenoid (the bolt that locks the door) | — | 1 = locked, 0 = unlocked |

### 0.4 Critical: the analogue setpoints are fail-safe CONSTANTS

The as-built values (Global Variables, verified in the export) are:

| Variable | Initial value | Block | Effect as exported |
| --- | --- | --- | --- |
| OXMON-01..04_SP | 25.0 | X_LimL (trips below) | top-of-range ⇒ oxygen trip always active |
| IT-01..03_SP, VT-01..03_SP | 0.0 | X_LimH (trips above) | zero ⇒ "source present" always active |
| all …_HYST | 0.2 | — | — |

Two consequences:

They are deliberately fail-safe placeholders — until commissioning sets

real values, the analogue functions sit in their tripped (safe) state.

They are declared `Constant` in the variable table — so in offline

simulation you cannot force `_SP`/`_HYST` at runtime. Forcing the field    value (e.g. IT-01 = 3.9) can therefore NEVER clear these trips (3.9 > 0.0).

Practical choices for offline simulation:

Option A (recommended, no code change): leave the values alone and

force the `_TRIP` BOOLs directly — OXMON-01..04_TRIP = 0,   IT-01..03_TRIP = 0, VT-01..03_TRIP = 0 for healthy; set individual ones   to 1 to simulate a trip. Forcing overrides the POU's write, so the SIF logic   downstream behaves exactly as designed. (You lose only the limit-block   internals, which Option B covers.)

Option B (to exercise the X_LimH/X_LimL blocks themselves): edit the

_SP initial values in the global-variable editor (e.g. OXMON_SP =   19.5, IT/VT_SP = 6.0), regenerate code, restart the simulation — then   field-value forcing works as in §2.1. Revert afterwards; on a real system   this is a controlled modification.

### 0.5 Concept: the timers run on the simulation clock

MAX_SEARCH_TIME = 180 s, six per-step windows 5 s…60 s, BEAM_DELAY = 180 s, DOOR_UNLOCK_DELAY = 20 s, LIGHT_CURTAIN_DELAY = 2 s, RESET_DELAY = 60 s, alarm dwell E_SOURCE_TIME = 120 s. In offline sim these elapse in (simulated) real time — between search steps wait ≥5 s and <60 s.

In plain words — what each timer is for. Think of each one as a stopwatch the safety PLC uses so things can't happen too fast or too slow:

| Timer | Value | What it does, in everyday terms |
| --- | --- | --- |
| MAX_SEARCH_TIME | 180 s (3 min) | The whole hutch search must be finished within 3 minutes, or it cancels and you start again. |
| per-step window | 5–60 s | Between each search button you must wait at least 5 seconds (so nobody can rush or "tailgate" the search) but no more than 60 seconds (so you can't wander off half-way). |
| BEAM_DELAY | 180 s (3 min) | Once the search is done, the system waits 3 minutes — with warning sirens and lights ("radiation imminent") — before it will switch the beam on, giving anyone still inside time to hit a beam-off button. |
| DOOR_UNLOCK_DELAY | 20 s | After the source reads zero, the PLC waits 20 seconds to be sure it is *really* off before it lets you unlock the doors. |
| LIGHT_CURTAIN_DELAY | 2 s | A short 2-second pause after someone steps through the doorway before the light curtain starts watching for extra people. |
| RESET_DELAY | 60 s (1 min) | A one-minute wait before the system settles back to the fully "Open" state. |
| E_SOURCE_TIME | 120 s (2 min) | How long the source must stay switched off before the alarm screen accepts it as truly dead. |

__________________________________________________

## 1 · Baseline (run before every test block)

Concept. Every test must start from a known-good plant: all doors shut, keys in, nothing pressed, process values healthy. The program shows this as STATUS-OPEN_READY = 1 ("ready to start a search").

Force TRUE (1): GADC-01..06, SADC-01..05, KEY-01, KEY-02, KEY-03, all sixteen BOB-0x:A/:B, LCRx-01. Force FALSE (0): ASB-01..04, ASBF-01, SCR-01, OR-01, GADL-01/02/04/05, SADL-01/02 (locks not yet engaged), radiation RDMND/RDMNR-01/02 healthy. Force the analogue trip flags FALSE (0) — per §0.4 Option A (the _SP constants make value-forcing ineffective): OXMON-01..04_TRIP = 0, IT-01..03_TRIP = 0, VT-01..03_TRIP = 0. *(Option B users: with edited setpoints, force IT/VT-0x = 3.9 and OXMON-0x = 20.9 instead.)* Pulse once: …-BOB:RESET, …-RDMN:RESET, …-GAS:RESET (clear power-up latches).

Expect: STATUS-OPEN_READY = 1; ANNOPN-01:A/:B = 1; every CON-0x:EN = 0; every SOL-0x = 0; all BL10E-SIF-0x_TRIP at their healthy value (mostly 1).

__________________________________________________

## 2 · Input-layer logic (how a field signal becomes a trip)

### 2.1 Concept: analogue channel → limit block → `_TRIP` flag

Each 4–20 mA input (oxygen, current, voltage) is scaled (X_Hx_AI, p.588) and fed to a limit block — X_LimH (p.507) trips above its setpoint (current, voltage), X_LimL (p.514) trips below it (oxygen). Each block has a setpoint …_SP, hysteresis …_HYST, a trip delay DT, and produces the BOOL …_TRIP. The channel also publishes _OC/_SC/_CH_OK (open/short-circuit, channel-OK) diagnostics.

This test requires §0.4 Option B (the _SP values are Constant — they cannot be forced). Edit the initial values in the global-variable editor (OXMON-01_SP = 19.5, IT-01_SP = 6.0 for this test), regenerate code and restart the simulation first. If you stay on Option A, skip Test 2.1 — the SIF-level behaviour is fully covered by forcing _TRIP in §3.

Test 2.1 — open Analogue Inputs logic (pp.184–187), with edited setpoints:

| Step | Force | Watch / expect |
| --- | --- | --- |
| 1 | OXMON-01 = 20.9 | OXMON-01_TRIP = 0 |
| 2 | OXMON-01 = 18.0 | OXMON-01_TRIP → 1 (low trip) |
| 3 | OXMON-01 = 19.6 (just above SP 19.5) | stays tripped until SP+HYST cleared — hysteresis |
| 4 | IT-01 = 12.0 | IT-01_TRIP → 1 (high trip) |

What it proves: you can trace any analogue from raw value to its _TRIP flag, and you understand setpoint + hysteresis.

### 2.2 Concept: dual-channel digital inputs and discrepancy

Safety pushbuttons (BOB) and indicators are two independent channels :A and :B, AND'd so a single wiring fault cannot fake a healthy button. A 2In_Discrepency_Alarm (def. pp.152–156; instantiated in Alarms, pp.171–174) raises an alarm if :A ≠ :B for longer than its delay — that is a fault, not a trip.

Test 2.2: force BOB-05:A = 0 while BOB-05:B = 1. Expect: SIF-08_TRIP behaviour per design (single-channel demand is still a demand — watch it live), and the BOB-05 discrepancy alarm in Alarms (p.171). Restore both to 1, reset. What it proves: channel-fault detection is separate from the trip function.

__________________________________________________

## 3 · The SIF tests (concept + logic + test, one by one)

Re-establish §1 between tests. Page references are the logic pages.

### SIF-01 — General Access Door (p.291)

Concept. If the main personnel door is open, the electron source must be isolated — radiation must never coexist with an open door. Three independent closed-switches on the door vote 2oo3: one broken/misaligned switch must not spuriously kill the beam (availability), two open switches must (safety). Logic as built. X_2oo3_B(GADC-01,02,03).Out & BL10E-SIF-07_OUTPUT → BL10E-SIF-01_TRIP (a permissive: 1 = healthy). The voter (p.644) sums the three BOOLs and outputs TRUE when ≥2 are TRUE; its Dev pin flags channel disagreement after delay DT. Test. From BEAM_ON (§4 walkthrough) or baseline:

| Step | Force | Expect |
| --- | --- | --- |
| 1 | GADC-01 = 0 | voter Out stays 1 — no trip (2oo3 tolerates one); after DT, voter Dev flags discrepancy |
| 2 | GADC-02 = 0 | voter Out → 0, SIF-01_TRIP → 0; `CON-01/02/03:EN → 0` (and CON-10:EN, same latch group, p.267) |
| 3 | restore both = 1 | contactors stay 0 — see §5 latch test |

### SIF-13 — General Access Gate (p.382)

Concept. Rev 4.0 split the gate from the door so each has its own function; the gate isolates the RF path with a deliberate 200 ms delay (ride-through for switch bounce on a moving gate). Logic. X_2oo3_B(GADC-04,05,06) & SIF-07_OUTPUT → SIF-13_TRIP. Test. GADC-04 = 0 (no trip) then GADC-05 = 0 → SIF-13_TRIP → 0; after ~200 ms `CON-06/07/08:EN → 0` (and CON-09:EN, same group, p.267).

### SIF-02 — Service Access Door (p.297)

Concept. The service door is a second personnel entry with its own switch sets: a 2oo3 triple plus a 1oo2 pair (different door leaf), OR'd — either voted-open isolates the source. Logic. (X_2oo3_B(SADC-01,02,03) & SADC-04 & SADC-05) & SIF-07_OUTPUT → SIF-02_TRIP, also publishes SERVICE_DOOR_CLOSED. Test A (2oo3): SADC-01 = 0, then SADC-02 = 0 → trip → CON-01/02/03 → 0. Test B (1oo2): baseline, then only SADC-04 = 0 → trips alone.

### SIF-03 — Current & Voltage monitoring / door-unlock permit (p.303)

Concept. Doors may only unlock when the source is provably dead. "Dead" is measured two independent ways — current (IT) and voltage (VT), each 2oo3 — and must hold for 20 s (DOOR_UNLOCK_DELAY) before the Open/Reset button is even enabled. Then a deliberate human action (OR-01) opens up. This prevents unlocking on a momentary dip or a single faulty transmitter. Logic. Two voters X_2oo3_B(IT-01..03_TRIP), X_2oo3_B_1(VT-01..03_TRIP), RS latch, TON(PT = T#20s), R_TRIG(OR-01), OR-01:LED = "press me now" lamp → BL10E-SIF-03_OUTPUT. Test.

| Step | Force (Option A: the _TRIP flags) | Expect |
| --- | --- | --- |
| 1 | IT-01_TRIP = 1, IT-02_TRIP = 1 | current voted present (2oo3) → locks SOL-0x held 1, OR-01:LED = 0 |
| 2 | IT-01_TRIP = 0, IT-02_TRIP = 0, wait <20 s | OR-01:LED still 0 (20 s confirm running) |
| 3 | wait ≥20 s | OR-01:LED → 1 |
| 4 | pulse OR-01 | SIF-03_OUTPUT permits unlock; SFC heads to OPEN (60 s RESET_DELAY) |
| 5 | repeat 1–4 with `VT-01_TRIP/VT-02_TRIP` | identical behaviour via the voltage voter |

*(Option B users: drive the same steps with field values instead — IT-0x = 12.0 for present, 3.9 for dead — after editing the setpoints.)*

### SIF-05 — Search Start permissive (p.344)

Concept. A search may only begin when one authorised person (card + both keys) starts it with the service doors already shut and no beam-off latched. Every condition is a hard gate — remove any one and the search must refuse to start. This is your negative-test set. Logic. SCR-01 & KEY-01 & KEY-02 & SADC-04 & SADC-05 & X_2oo3_B(SADC-01..03) & SIF-08_TRIP → SIF-05_START (single AND gate — beautifully readable on p.344). Test. From baseline, for each row force the one item, then SCR-01 = 1:

| Blocked by | Force | Expect |
| --- | --- | --- |
| (control) nothing | just SCR-01 = 1 | SIF-05_START → 1, STATUS-START_SEARCH → 1 ✔ |
| key 1 out | KEY-01 = 0 | SIF-05_START stays 0 — no search |
| key 2 out | KEY-02 = 0 | stays 0 |
| service door open | SADC-04 = 0 | stays 0 |
| BOB latched | press+release a BOB, no reset | stays 0 until …BOB:RESET pulsed |

### SIF-06 — Search Complete proof (p.350)

Concept. The final search button only counts if every general door and gate is shut at that instant — otherwise someone could still slip in. Logic. X_2oo3_B(GADC-01..03) & X_2oo3_B_1(GADC-04..06) → SIF-06_TRIP (+ GENERAL_ACCESS_DOOR_CLOSED, and SIF-06_OUTPUT which sets the door-lock solenoid latch in Logic p.267). Test. During the walkthrough (§4) at step ASB4: force GADC-01 = 0 and GADC-02 = 0, pulse ASBF-01 → T7 refused (SIF-06_TRIP = 0, no STANDBY). Close the doors, pulse ASBF-01 again → STANDBY.

### SIF-07 — Beam-On permissive / lock feedback + 180 s (p.356)

Concept. Locked doors must be proven, not assumed: the *feedback* switches on each lock (not the command) gate the beam permit, and a 180 s "radiation imminent" dwell (BEAM_DELAY_TIMER) gives anyone inside a last chance to hit a beam-off button. Command ≠ confirmation — core safety idea. Logic. GADL-01 & GADL-02 & GADL-05 & GADL-04 & SADL-01 & SADL-02 & SIF-06_TRIP/_OUTPUT → TON(BEAM_DELAY_TIMER_TIME = 180 s) + RS → BEAM_DELAY_TIMER_END / SIF-07_OUTPUT. Test (positive). In §4 after T7: force the six feedbacks GADL-01/02/04/05, SADL-01/02 = 1 (simulating the mechanisms), wait 180 s → BEAM_DELAY_TIMER_END → 1, SIF-07_OUTPUT → 1. Test (negative). Repeat the walkthrough but leave `SADL-02 = 0` (one lock fails to engage). Expect: SIF-07_OUTPUT stays 0, no BEAM_ON ever — this is the test v1 of this document was missing.

### SIF-08 — Beam-Off Buttons (p.363)

Concept. The emergency stop. Eight dual-channel buttons, any one (1oo7) kills source *and* RF (two independent hazard paths = "defence in depth") and unlocks the doors so people can escape. It latches: releasing the button must never restart a hazard — only a deliberate, separate reset may clear it. Logic. Per button :A & :B; all buttons into an RS latch; reset = …-BOB:RESET; output SIF-08_TRIP (permissive). Test.

| Step | Force | Expect |
| --- | --- | --- |
| 1 | BOB-03:A = 0 and BOB-03:B = 0 | SIF-08_TRIP → 0; CON-01,02,03,06,07,08,09,10:EN → 0; locks SOL-0x → 0 (instant escape unlock, C&E footnote a) |
| 2 | restore both = 1 | SIF-08_TRIP stays 0 (latched) |
| 3 | pulse …-BOB:RESET | SIF-08_TRIP → 1 (hazard still off — needs new search) |
| 4 | repeat for buttons 1,2,4,5,6,7,8 | each alone trips (1oo7) |

### SIF-09 — Radiation monitors (p.368)

Concept. Two independent monitors, each giving accumulated dose (RDMND) and dose-rate (RDMNR) signals; 1oo2 because a real radiation alarm must never be out-voted. Latched, with its own reset, so a transient can't self-clear. Logic. (RDMND-01, RDMNR-01, RDMND-02, RDMNR-02) → 1oo2 gating → RS latch, reset …-RDMN:RESET → SIF-09_TRIP. Test. Force RDMND-01 to trip → SIF-09_TRIP → 0 → CON-01/02/03 → 0 (+ CON-10, latch group). Restore; still tripped; pulse …-RDMN:RESET → clears. Repeat with RDMNR-01, RDMND-02, RDMNR-02.

### SIF-10 — Electron-Source Enable Key (p.372)

Concept. A physical key (kept by the responsible person) is the authorisation to have the source/RF energisable at all. 1oo1 — no voting, the key is the law. A returned key is not a reset. Logic. KEY-03 → SIF-10_TRIP; gates CON-04/05 (with SIF-08) and the RF group (p.267). Test. From BEAM_ON: KEY-03 = 0 → SIF-10_TRIP → 0 → CON-04/05:EN → 0 (watch which RF contactors follow on p.267). KEY-03 = 1 → hazard stays off; recover only via new search.

### SIF-11 — Oxygen monitoring (p.377)

Concept. Cryogenic nitrogen can displace air; any one of four monitors reading low (1oo4 — maximum sensitivity, people pass out without warning) closes the LN₂ supply valve and drives the O₂ alarm state. Latched + own reset. Logic. OXMON-01..04_TRIP → ≥1 → RS latch, reset …-GAS:RESET → SIF-11_TRIP → SDVLN2, O₂ beacons (SP01/02-04..07), indicators. Test (Option A). OXMON-02_TRIP = 1 → SDVLN2 → 0 (valve shut), O₂ beacons to alarm. OXMON-02_TRIP = 0 → still latched. Pulse …-GAS:RESET → clears. Repeat each monitor (1oo4). *(Option B: use OXMON-02 = 18.0 / 20.9 after editing the setpoint.)*

__________________________________________________

## 4 · The search walkthrough (SIF-04 SFC, pp.326–338) — full pass to BEAM_ON

Concept. The SFC is the choreography that proves "nobody inside": one person sweeps the hutch pressing buttons in a fixed deep-to-door order. Two timing layers police it: the overall 180 s MAX_SEARCH_TIME, and per-step Transition_Timers (p.285) with Min 5 s / Max 60 s — too fast means you didn't actually look (or two people are gaming it), too slow means lost control of the area. The light curtain counts entries: exactly one pass in, then any further beam break during T2–T6 aborts.

Watch list: STATUS-OPEN_READY/-START_SEARCH/-HUTCH_ENTERED/-ASB1..4/ -STANDBY/-BEAM_ON, SEARCHED_AND_LOCKED, SEARCH_TIMER_RUNNING, SEARCH_TIME_EXCEEDED, LIGHT_CURTAIN_MONITORING, BEAM_DELAY_TIMER_END, ABORT_SEARCH, Tx-Ty_TIMER_TRIP_LOW/HIGH, SIF-05_START, SIF-06_TRIP, SIF-07_OUTPUT.

| # | You force | State advances to | Also watch |
| --- | --- | --- | --- |
| 0 | §1 baseline | STATUS-OPEN_READY = 1 | — |
| T1 | SCR-01 = 1 | START_SEARCH | SIF-05_START → 1; SOL-05/06 → 1 (service locks); force `SADL-01/02 = 1` (feedback follows); ANNRES = 1; 180 s timer runs |
| — | wait ≥5 s | — | T1-T2_TIMER running |
| T2 | pulse LCRx-01: 1→0→1 | HUTCH_ENTERED | after 2 s LIGHT_CURTAIN_MONITORING → 1 |
| — | wait ≥5 s | — | — |
| T3 | pulse ASB-01: 0→1→0 | ASB1 | ASB-01:LED = 1 |
| — | wait ≥5 s | — | — |
| T4 | pulse ASB-02 | ASB2 | ASB-02:LED = 1 |
| — | wait ≥5 s | — | — |
| T5 | pulse ASB-03 | ASB3 | ASB-03:LED = 1 |
| — | wait ≥5 s | — | — |
| T6 | pulse ASB-04 | ASB4 | ASB-04:LED = 1; LC monitoring ends |
| — | wait ≥5 s | — | — |
| T7 | pulse ASBF-01 (needs SIF-06_TRIP = 1) | STANDBY | SOL-01..04 → 1; force `GADL-01/02/04/05 = 1` ← *without this the sequence stalls here*; ANNSTB = 1; BLUEL-0x = 1; SEARCHED_AND_LOCKED → 1; beacon SP02 |
| — | wait 180 s | — | BEAM_DELAY_TIMER_END → 1, SIF-07_OUTPUT → 1 |
| T8 | (transition fires) | BEAM_ON | ANNBON = 1; BONI-01:A/:B = 1; `CON-0x:EN → 1`; white lights pulse (TP T#1s, p.337); KEY-01:SOL releases |

### 4.1 Abort tests (each must land in an `*_ABORTED` path / back toward OPEN)

| Abort | Provoke | Watch |
| --- | --- | --- |
| Out of order | at START_SEARCH pulse ASB-01 before LCRx | ABORT_SEARCH → 1 |
| Too fast | next step <5 s after previous | that Tx-Ty_TIMER_TRIP_LOW → 1 → abort |
| Too slow | sit in a step >60 s | Tx-Ty_TIMER_TRIP_HIGH → 1 → abort |
| Whole search >180 s | dawdle overall | SEARCH_TIME_EXCEEDED → 1 → abort |
| Light curtain re-break | during T3..T6 pulse LCRx-01 = 0 | abort while LIGHT_CURTAIN_MONITORING = 1 |
| Key pulled mid-search | KEY-01 = 0 (or KEY-02) before T7 | abort |
| Door mid-search | GADC-01 = 0 + GADC-02 = 0 | abort |
| Door at the final button | doors open at ASB4, pulse ASBF-01 | T7 refused (SIF-06_TRIP = 0) |

### 4.2 KEY-01 release behaviour (C&E footnote k / p.337)

Concept. KEY-01 is trapped (solenoid) during the search; at BEAM_ON the program releases it so it can be carried to the rack position (KEY-03). Removing it *before* the search completes must abort; removing it *after* release must not. Test. (a) Mid-search KEY-01 = 0 → abort (done in 4.1). (b) Reach BEAM_ON, watch KEY-01:SOL → 0 (released).

__________________________________________________

## 5 · The no-silent-restart latch (`Logic` p.267) — the most important test

Concept. After any trip, clearing the cause must not re-energise the hazard. The contactor logic AND's the SIF permissives with SEARCHED_AND_LOCKED & STATUS-BEAM_ON through RS latches. The page carries this exact comment:

*"If Search and Locked is broken, contactors 01, 02, 03, 06, 07, 08, 09 & 10 can not start again when tripped without going through a new search sequence."*

Verified groupings (p.267):

| Latch group | Contactors | Gated by |
| --- | --- | --- |
| Source group | CON-01, 02, 03, 10 | SIF-08 & SIF-01 & SIF-02 & SIF-09 + SEARCHED_AND_LOCKED & STATUS-BEAM_ON |
| Gate/RF group | CON-06, 07, 08, 09 | SIF-13 (+ customer interlock CUST-01 path) |
| Key group | CON-04, 05 | SIF-10 & SIF-08 |
| Door locks | SOL-01..06 | set by R_TRIG(SIF-06_OUTPUT) (T1: service / T7: general), reset by STATUS-OPEN or SIF-08 trip |

Test. Reach BEAM_ON → trip anything (e.g. one BOB) → clear it → reset → confirm every contactor in the latch groups stays 0 → only a complete new §4 walkthrough re-energises. Do this once with a door trip and once with a BOB trip.

__________________________________________________

## 6 · The alarm/diagnostic layer (pp.162–174) — monitoring, not tripping

Concept. Around the SIFs sits a non-tripping layer that tells the operator *why* something happened: per-channel _ALARM flags (e.g. IT-0x_TRIP through a TOF with E_SOURCE_TIME = 120 s, p.172), dual/triple-channel discrepancy alarms (pp.171, 173–174), and system diagnostics (PSU/fan/ switch faults on DI-007, forcing-active flags, module errors — Diagnostics pp.241–250). These drive annunciation only. Test (sample). Force IT-01 = 12 for >120 s → IT-01_ALARM sets; restore → alarm clears after the TOF. Force GADC-01 = 0 alone for > voter DT → X_2oo3_B.Dev discrepancy flag (door switch disagreement = maintenance alarm).

__________________________________________________

## 7 · Coverage matrix (tick when done)

| # | Logic under test | Where | Concept proven |
| --- | --- | --- | --- |
| 2.1 | Analogue channel → _TRIP | pp.184–187 | scaling, setpoint, hysteresis |
| 2.2 | Dual-channel + discrepancy | pp.152–161, 171–174 | channel fault ≠ trip |
| 3 | SIF-01 door | p.291 | 2oo3 voting |
| 3 | SIF-13 gate | p.382 | 2oo3 + 200 ms |
| 3 | SIF-02 service door | p.297 | 2oo3 OR 1oo2 |
| 3 | SIF-03 IT+VT unlock permit | p.303 | 2×2oo3, 20 s confirm, manual OR |
| 3 | SIF-05 start permissive (5 negatives) | p.344 | AND-gate authorisation |
| 3 | SIF-06 search-complete proof | p.350 | doors closed at T7 |
| 3 | SIF-07 lock feedback + 180 s (pos+neg) | p.356 | command ≠ confirmation |
| 3 | SIF-08 BOB ×8 | p.363 | 1oo7, latch, escape unlock |
| 3 | SIF-09 radiation ×4 signals | p.368 | 1oo2, latch |
| 3 | SIF-10 key | p.372 | 1oo1, key ≠ reset |
| 3 | SIF-11 oxygen ×4 | p.377 | 1oo4, latch |
| 4 | Full SFC T1→T8 | pp.326–338 | the search choreography |
| 4.1 | 8 abort cases | pp.328–331 | both timing layers + monitors |
| 4.2 | KEY-01 trap/release | p.337 | search integrity |
| 5 | No-silent-restart latches | p.267 | the master safety property |
| 6 | Alarm layer | pp.162–174 | diagnosis vs protection |

## 8 · Known limits / honest notes

The analogue setpoints are fail-safe constants (OXMON_SP = 25.0,

IT/VT_SP = 0.0) — they cannot be forced; see §0.4 for the two ways to test   around them. The illustrative commissioning values used in the companion docs   (19.5 %O₂, >4 mA) come from the C&E, not from the program.

A few exact pin polarities are hard to read from the flattened export (e.g.

inverter bubbles): trust the live values in simulation, that's what it's for.

The SRS (TDI-PSS-SRS-0002) and SIF drawing (Dwg 1224211) are not in the

repo; for plant work reconcile against them (e.g. C&E note says 12 s where the   program implements DOOR_UNLOCK_DELAY = 20 s).

## 9 · Test record template

Test ref (matrix #): ____  Page: ____  Date: ____  Engineer: ____
Baseline OK (STATUS-OPEN_READY=1)?  Y / N
Setpoints forced (_SP values): ______________________________
Forced (tag = value): _______________________________________
Intermediate (tag : observed): ______________________________
Output (tag : observed): ____________________________________
Latched? reset used: ____________  New search needed?  Y / N
PASS / FAIL: ____  Notes: ___________________________________