## Cover Sheet
Doc Title: |  | HeXI I/O Schedule
Doc No: |  | C15862H-HEXI-IOS |  | Rev: | 0/2
Client: |  | Diamond Light Source Limited
Project: |  | HIMax System
Description: |  | Safety Instrumented System for Three Flagship Beamlines and HeXI |  |  |  | SC Ref:
PO No: |  | 9001537/8046970/9003503 |  |  |  | C15862H
B10 E - HeXI Safety Instrumented System
I/O Schedule
| 0/2 | 2026-04-16 | Client Mods |  |  | CW
| 0 | 2026-02-11 | First Issue | EF | NPB | CW
| Revision | Date | Description | By | Chk | App
Carrington Field Street ¦ Stockport ¦ Cheshire ¦ SK1 3JN
Tel: 0161 429 4500 ¦ Fax: 0161 476 3095 ¦ Email: admin@sellacontrols.com ¦ Web: www.sellacontrols.com

## 005_AI
TAG | DESCRIPTION | SIGNAL TYPE | CHASSIS &SLOT No | Channel No. | Signal | MODULE | CONNECTION BOARD | CB TERM. | DEVICE LOCATION | DEVICE TAG | WIRE COLOUR | WIRE TYPE | WIRE NUMBER | TERMINAL BLOCK | TERM. No. | Loop Type | REV.
B10E-PS-OXMON-01 | Oxygen Monitor 01 | 4-20mA | 005 | 1 | S1+ | X-AI 32 02 | X-CB 008 01 | 01a | HUTCH | B10E-PS-OXMON-01 |  | 3 x 0.5mm² LSZH |  |  |  | AI2 | 0
[5 empty] | AI1+ |  |  | 01b |  |  | White (tri cable) |  | 005/AI1+ | X-OXMON | 3
[5 empty] | AI1- |  |  | 01c
[5 empty] | 12L+/14 | [5 empty] | Brown (tri cable) |  | 12L+/14 | X-OXMON | 1
[5 empty] | 12L-/14 | [5 empty] | Green (tri cable) |  | 12L-/14 | X-OXMON | 4
B10E-PS-OXMON-02 | Oxygen Monitor 02 | 4-20mA | 005 | 2 | S2+ | X-AI 32 02 | X-CB 008 01 | 02a | HUTCH | B10E-PS-OXMON-02 |  | 3 x 0.5mm² LSZH |  |  |  | AI2 | 0
[5 empty] | AI2+ |  |  | 02b |  |  | White (tri cable) |  | 005/AI2+ | X-OXMON | 7
[5 empty] | AI2- |  |  | 02c
[5 empty] | 12L+/14 | [5 empty] | Brown (tri cable) |  | 12L+/14 | X-OXMON | 5
[5 empty] | 12L-/14 | [5 empty] | Green (tri cable) |  | 12L-/14 | X-OXMON | 8
B10E-PS-OXMON-03 | Oxygen Monitor 03 | 4-20mA | 005 | 3 | S3+ | X-AI 32 02 | X-CB 008 01 | 03a | HUTCH | B10E-PS-OXMON-03 |  | 3 x 0.5mm² LSZH |  |  |  | AI2 | 0/1
[5 empty] | AI3+ |  |  | 03b |  |  | White (tri cable) |  | 005/AI3+ | X-OXMON | 11
[5 empty] | AI3- |  |  | 03c
[5 empty] | 12L+/15 | [5 empty] | Brown (tri cable) |  | 12L+/15 | X-OXMON | 9
[5 empty] | 12L-/15 | [5 empty] | Green (tri cable) |  | 12L-/15 | X-OXMON | 12
B10E-PS-OXMON-04 | Oxygen Monitor 04 | 4-20mA | 005 | 4 | S4+ | X-AI 32 02 | X-CB 008 01 | 04a | HUTCH | B10E-PS-OXMON-04 |  | 3 x 0.5mm² LSZH |  |  |  | AI2 | 0/1
[5 empty] | AI4+ |  |  | 04b |  |  | White (tri cable) |  | 005/AI4+ | X-OXMON | 15
[5 empty] | AI4- |  |  | 04c
[5 empty] | 12L+/15 | [5 empty] | Brown (tri cable) |  | 12L+/15 | X-OXMON | 13
[5 empty] | 12L-/15 | [5 empty] | Green (tri cable) |  | 12L-/15 | X-OXMON | 16
SPAI-005/5 | Wired Spare Input | 4-20mA | 005 | 5 | S5+ | X-AI 32 02 | X-CB 008 01 | 05a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S5+ | X-SPAI | 1 | AI1 | 0/1 | Removed
[5 empty] | AI5+ |  |  | 05b |  |  | White (tri cable) |  | 005/AI5+ | X-SPAI | 2
[5 empty] | AI5- |  |  | 05c |  |  | Green (tri cable) |  | 005/AI5- | X-SPAI | 3
SPAI-005/6 | Wired Spare Input | 4-20mA | 005 | 6 | S6+ | X-AI 32 02 | X-CB 008 01 | 06a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S6+ | X-SPAI | 4 | AI1 | 0/1 | Removed
[5 empty] | AI6+ |  |  | 06b |  |  | White (tri cable) |  | 005/AI6+ | X-SPAI | 5
[5 empty] | AI6- |  |  | 06c |  |  | Green (tri cable) |  | 005/AI6- | X-SPAI | 6
B10E-PS-IT-01 | Current Transmitter L1 (E. Source) | 4-20mA | 005 | 7 | S7+ | X-AI 32 02 | X-CB 008 01 | 07a | ELECTRON SOURCE | B10E-PS-IT-01 | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S7+ | X-INTF07 | 21 | AI1 | 0
[5 empty] | AI7+ |  |  | 07b |  |  | White (tri cable) |  | 005/AI7+ | X-INTF07 | 22
[5 empty] | AI7- |  |  | 07c |  |  | Green (tri cable) |  | 005/AI7- | X-INTF07 | 23
B10E-PS-IT-02 | Current Transmitter L2 (E. Source) | 4-20mA | 005 | 8 | S8+ | X-AI 32 02 | X-CB 008 01 | 08a | ELECTRON SOURCE | B10E-PS-IT-02 | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S8+ | X-INTF07 | 24 | AI1 | 0
[5 empty] | AI8+ |  |  | 08b |  |  | White (tri cable) |  | 005/AI8+ | X-INTF07 | 25
[5 empty] | AI8- |  |  | 08c |  |  | Green (tri cable) |  | 005/AI8- | X-INTF07 | 26
B10E-PS-IT-03 | Current Transmitter L3 (E. Source) | 4-20mA | 005 | 9 | S9+ | X-AI 32 02 | X-CB 008 01 | 09a | ELECTRON SOURCE | B10E-PS-IT-03 | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S9+ | X-INTF07 | 27 | AI1 | 0
[5 empty] | AI9+ |  |  | 09b |  |  | White (tri cable) |  | 005/AI9+ | X-INTF07 | 28
[5 empty] | AI9- |  |  | 09c |  |  | Green (tri cable) |  | 005/AI9- | X-INTF07 | 29
B10E-PS-VT-01 | Voltage Transmitter L1 (E. Source) | 4-20mA | 005 | 10 | S10+ | X-AI 32 02 | X-CB 008 01 | 10a | ELECTRON SOURCE | B10E-PS-VT-01 | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S10+ | X-INTF07 | 30 | AI1 | 0/2 | Rewire
[5 empty] | AI10+ |  |  | 10b |  |  | White (tri cable) |  | 005/AI10+ | X-INTF07 | 31
[5 empty] | AI10- |  |  | 10c |  |  | Green (tri cable) |  | 005/AI10- | X-INTF07 | 32
B10E-PS-VT-02 | Voltage Transmitter L2 (E. Source) | 4-20mA | 005 | 11 | S11+ | X-AI 32 02 | X-CB 008 01 | 11a | ELECTRON SOURCE | B10E-PS-VT-02 | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S11+ | X-INTF07 | 33 | AI1 | 0/2 | Rewire
[5 empty] | AI11+ |  |  | 11b |  |  | White (tri cable) |  | 005/AI11+ | X-INTF07 | 34
[5 empty] | AI11- |  |  | 11c |  |  | Green (tri cable) |  | 005/AI11- | X-INTF07 | 35
B10E-PS-VT-03 | Voltage Transmitter L3 (E. Source) | 4-20mA | 005 | 12 | S12+ | X-AI 32 02 | X-CB 008 01 | 12a | ELECTRON SOURCE | B10E-PS-VT-03 | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S12+ | X-INTF07 | 36 | AI1 | 0/2 | Rewire
[5 empty] | AI12+ |  |  | 12b |  |  | White (tri cable) |  | 005/AI12+ | X-INTF07 | 37
[5 empty] | AI12- |  |  | 12c |  |  | Green (tri cable) |  | 005/AI12- | X-INTF07 | 38
SPAI-005/15 | Wired Spare Input | 4-20mA | 005 | 13 | S13+ | X-AI 32 02 | X-CB 008 01 | 13a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S13+ | X-SPAI | 7 | AI1 | 0/1 | Removed
[5 empty] | AI13+ |  |  | 13b |  |  | White (tri cable) |  | 005/AI13+ | X-SPAI | 8
[5 empty] | AI13- |  |  | 13c |  |  | Green (tri cable) |  | 005/AI13- | X-SPAI | 9
SPAI-005/16 | Wired Spare Input | 4-20mA | 005 | 14 | S14+ | X-AI 32 02 | X-CB 008 01 | 14a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S14+ | X-SPAI | 10 | AI1 | 0/1 | Removed
[5 empty] | AI14+ |  |  | 14b |  |  | White (tri cable) |  | 005/AI14+ | X-SPAI | 11
[5 empty] | AI14- |  |  | 14c |  |  | Green (tri cable) |  | 005/AI14- | X-SPAI | 12
SPAI-005/15 | Wired Spare Input | 4-20mA | 005 | 15 | S15+ | X-AI 32 02 | X-CB 008 01 | 15a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S15+ | X-SPAI | 13 | AI1 | 0/1
[5 empty] | AI15+ |  |  | 15b |  |  | White (tri cable) |  | 005/AI15+ | X-SPAI | 14
[5 empty] | AI15- |  |  | 15c |  |  | Green (tri cable) |  | 005/AI15- | X-SPAI | 15
SPAI-005/16 | Wired Spare Input | 4-20mA | 005 | 16 | S16+ | X-AI 32 02 | X-CB 008 01 | 16a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S16+ | X-SPAI | 16 | AI1 | 0/1
[5 empty] | AI16+ |  |  | 16b |  |  | White (tri cable) |  | 005/AI16+ | X-SPAI | 17
[5 empty] | AI16- |  |  | 16c |  |  | Green (tri cable) |  | 005/AI16- | X-SPAI | 18
SPAI-005/17 | Wired Spare Input | 4-20mA | 005 | 17 | S17+ | X-AI 32 02 | X-CB 008 01 | 17a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S17+ | X-SPAI | 19 | AI1 | 0/1
[5 empty] | AI17+ |  |  | 17b |  |  | White (tri cable) |  | 005/AI17+ | X-SPAI | 20
[5 empty] | AI17- |  |  | 17c |  |  | Green (tri cable) |  | 005/AI17- | X-SPAI | 21
SPAI-005/18 | Wired Spare Input | 4-20mA | 005 | 18 | S18+ | X-AI 32 02 | X-CB 008 01 | 18a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S18+ | X-SPAI | 22 | AI1 | 0/1
[5 empty] | AI18+ |  |  | 18b |  |  | White (tri cable) |  | 005/AI18+ | X-SPAI | 23
[5 empty] | AI18- |  |  | 18c |  |  | Green (tri cable) |  | 005/AI18- | X-SPAI | 24
SPAI-005/19 | Wired Spare Input | 4-20mA | 005 | 19 | S19+ | X-AI 32 02 | X-CB 008 01 | 19a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S19+ | X-SPAI | 25 | AI1 | 0/1
[5 empty] | AI19+ |  |  | 19b |  |  | White (tri cable) |  | 005/AI19+ | X-SPAI | 26
[5 empty] | AI19- |  |  | 19c |  |  | Green (tri cable) |  | 005/AI19- | X-SPAI | 27
SPAI-005/20 | Wired Spare Input | 4-20mA | 005 | 20 | S20+ | X-AI 32 02 | X-CB 008 01 | 20a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S20+ | X-SPAI | 28 | AI1 | 0/1
[5 empty] | AI20+ |  |  | 20b |  |  | White (tri cable) |  | 005/AI20+ | X-SPAI | 29
[5 empty] | AI20- |  |  | 20c |  |  | Green (tri cable) |  | 005/AI20- | X-SPAI | 30
SPAI-005/21 | Wired Spare Input | 4-20mA | 005 | 21 | S21+ | X-AI 32 02 | X-CB 008 01 | 21a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S21+ | X-SPAI | 31 | AI1 | 0/1
[5 empty] | AI21+ |  |  | 21b |  |  | White (tri cable) |  | 005/AI21+ | X-SPAI | 32
[5 empty] | AI21- |  |  | 21c |  |  | Green (tri cable) |  | 005/AI21- | X-SPAI | 33
SPAI-005/22 | Wired Spare Input | 4-20mA | 005 | 22 | S22+ | X-AI 32 02 | X-CB 008 01 | 22a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S22+ | X-SPAI | 34 | AI1 | 0/1
[5 empty] | AI22+ |  |  | 22b |  |  | White (tri cable) |  | 005/AI22+ | X-SPAI | 35
[5 empty] | AI22- |  |  | 22c |  |  | Green (tri cable) |  | 005/AI22- | X-SPAI | 36
SPAI-005/23 | Wired Spare Input | 4-20mA | 005 | 23 | S23+ | X-AI 32 02 | X-CB 008 01 | 23a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S23+ | X-SPAI | 37 | AI1 | 0/1
[5 empty] | AI23+ |  |  | 23b |  |  | White (tri cable) |  | 005/AI23+ | X-SPAI | 38
[5 empty] | AI23- |  |  | 23c |  |  | Green (tri cable) |  | 005/AI23- | X-SPAI | 39
SPAI-005/24 | Wired Spare Input | 4-20mA | 005 | 24 | S24+ | X-AI 32 02 | X-CB 008 01 | 24a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S24+ | X-SPAI | 40 | AI1 | 0/1
[5 empty] | AI24+ |  |  | 24b |  |  | White (tri cable) |  | 005/AI24+ | X-SPAI | 41
[5 empty] | AI24- |  |  | 24c |  |  | Green (tri cable) |  | 005/AI24- | X-SPAI | 42
SPAI-005/25 | Wired Spare Input | 4-20mA | 005 | 25 | S25+ | X-AI 32 02 | X-CB 008 01 | 25a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S25+ | X-SPAI | 43 | AI1 | 0/1
[5 empty] | AI25+ |  |  | 25b |  |  | White (tri cable) |  | 005/AI25+ | X-SPAI | 44
[5 empty] | AI25- |  |  | 25c |  |  | Green (tri cable) |  | 005/AI25- | X-SPAI | 45
SPAI-005/26 | Wired Spare Input | 4-20mA | 005 | 26 | S26+ | X-AI 32 02 | X-CB 008 01 | 26a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S26+ | X-SPAI | 46 | AI1 | 0/1
[5 empty] | AI26+ |  |  | 26b |  |  | White (tri cable) |  | 005/AI26+ | X-SPAI | 47
[5 empty] | AI26- |  |  | 26c |  |  | Green (tri cable) |  | 005/AI26- | X-SPAI | 48
SPAI-005/27 | Wired Spare Input | 4-20mA | 005 | 27 | S27+ | X-AI 32 02 | X-CB 008 01 | 27a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S27+ | X-SPAI | 49 | AI1 | 0/1
[5 empty] | AI27+ |  |  | 27b |  |  | White (tri cable) |  | 005/AI27+ | X-SPAI | 50
[5 empty] | AI27- |  |  | 27c |  |  | Green (tri cable) |  | 005/AI27- | X-SPAI | 51
SPAI-005/28 | Wired Spare Input | 4-20mA | 005 | 28 | S28+ | X-AI 32 02 | X-CB 008 01 | 28a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S28+ | X-SPAI | 52 | AI1 | 0/1
[5 empty] | AI28+ |  |  | 28b |  |  | White (tri cable) |  | 005/AI28+ | X-SPAI | 53
[5 empty] | AI28- |  |  | 28c |  |  | Green (tri cable) |  | 005/AI28- | X-SPAI | 54
SPAI-005/29 | Wired Spare Input | 4-20mA | 005 | 29 | S29+ | X-AI 32 02 | X-CB 008 01 | 29a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S29+ | X-SPAI | 55 | AI1 | 0/1
[5 empty] | AI29+ |  |  | 29b |  |  | White (tri cable) |  | 005/AI29+ | X-SPAI | 56
[5 empty] | AI29- |  |  | 29c |  |  | Green (tri cable) |  | 005/AI29- | X-SPAI | 57
SPAI-005/30 | Wired Spare Input | 4-20mA | 005 | 30 | S30+ | X-AI 32 02 | X-CB 008 01 | 30a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S30+ | X-SPAI | 58 | AI1 | 0/1
[5 empty] | AI30+ |  |  | 30b |  |  | White (tri cable) |  | 005/AI30+ | X-SPAI | 59
[5 empty] | AI30- |  |  | 30c |  |  | Green (tri cable) |  | 005/AI30- | X-SPAI | 60
SPAI-005/31 | Wired Spare Input | 4-20mA | 005 | 31 | S31+ | X-AI 32 02 | X-CB 008 01 | 31a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S31+ | X-SPAI | 61 | AI1 | 0/1
[5 empty] | AI31+ |  |  | 31b |  |  | White (tri cable) |  | 005/AI31+ | X-SPAI | 62
[5 empty] | AI31- |  |  | 31c |  |  | Green (tri cable) |  | 005/AI31- | X-SPAI | 63
SPAI-005/32 | Wired Spare Input | 4-20mA | 005 | 32 | S32+ | X-AI 32 02 | X-CB 008 01 | 32a |  |  | Brown (tri cable) | 3 x 0.5mm² LSZH | 005/S32+ | X-SPAI | 64 | AI1 | 0/1
[5 empty] | AI32+ |  |  | 32b |  |  | White (tri cable) |  | 005/AI32+ | X-SPAI | 65
[5 empty] | AI32- |  |  | 32c |  |  | Green (tri cable) |  | 005/AI32- | X-SPAI | 66

## 007_DI
TAG | DESCRIPTION | SIGNAL TYPE | CHASSIS &SLOT No | Channel. No. | Signal | MODULE | CONNECTION BOARD | CB TERM. | DEVICE LOCATION | DEVICE TAG | WIRE COLOUR | WIRE TYPE | WIRE NUMBER | TERMINAL BLOCK | TERM. No. | Loop Type | REV.
B10E-PS-FNFLT-01 | Himax Fan Fault | 24Vdc | 007 | 1 | S1+ | X-DI 32 05 | X-CB 005 01 | 1a | LOGIC SOLVER | B10E-PS-FAN-01 | Red | 0.5mm² H05Z-K | 007/S1+ | FAN-0 | 8 | DI2 | 0
[5 empty] | DI1+ |  |  | 1b |  |  | Grey | 0.5mm² H05Z-K | 007/DI1+ | FAN-0 | 9
B10E-PS-IOC-01:SYSTEMP | Rack Internal Temperature Alarm | 24Vdc | 007 | 2 | S2+ | X-DI 32 05 | X-CB 005 01 | 2a | LOGIC SOLVER | B10E-PS-STAT-1 | Red | 0.5mm² H05Z-K | 007/S2+ | STAT-1 | 3 | DI2 | 0
[5 empty] | DI2+ |  |  | 2b |  |  | Grey | 0.5mm² H05Z-K | 007/DI2+ | STAT-1 | 5
B10E-PS-PSU-01:A1:FAULT | 24VDC PSU A1 Fault | 24Vdc | 007 | 3 | S3+ | X-DI 32 05 | X-CB 005 01 | 3a | LOGIC SOLVER | B10E-PS-PSU-01:A1 | Red | 0.5mm² H05Z-K | 007/S3+ | PSU-A1 | 13 | DI2 | 0
[5 empty] | DI3+ |  |  | 3b |  |  | Grey | 0.5mm² H05Z-K | 007/DI3+ | PSU-A1 | 14
B10E-PS-PSU-01:A2:FAULT | 24VDC PSU A2 Fault | 24Vdc | 007 | 4 | S4+ | X-DI 32 05 | X-CB 005 01 | 4a | LOGIC SOLVER | B10E-PS-PSU-01:A2 | Red | 0.5mm² H05Z-K | 007/S4+ | PSU-A2 | 13 | DI2 | 0
[5 empty] | DI4+ |  |  | 4b |  |  | Grey | 0.5mm² H05Z-K | 007/DI4+ | PSU-A2 | 14
B10E-PS-PSU-01:A3:FAULT | 24VDC PSU A3 Fault | 24Vdc | 007 | 5 | S5+ | X-DI 32 05 | X-CB 005 01 | 5a | LOGIC SOLVER | B10E-PS-PSU-01:B1 | Red | 0.5mm² H05Z-K | 007/S5+ | PSU-A3 | 13 | DI2 | 0/1 | Add
[5 empty] | DI5+ |  |  | 5b |  |  | Grey | 0.5mm² H05Z-K | 007/DI5+ | PSU-A3 | 14
B10E-PS-PSU-01:B1:FAULT | 24VDC PSU B1 Fault | 24Vdc | 007 | 6 | S6+ | X-DI 32 05 | X-CB 005 01 | 6a | LOGIC SOLVER | B10E-PS-PSU-01:B2 | Red | 0.5mm² H05Z-K | 007/S6+ | PSU-B1 | 13 | DI2 | 0/1 | Moved
[5 empty] | DI6+ |  |  | 6b |  |  | Grey | 0.5mm² H05Z-K | 007/DI6+ | PSU-B1 | 14
B10E-PS-PSU-01:B2:FAULT | 24VDC PSU B2 Fault | 24Vdc | 007 | 7 | S7+ | X-DI 32 05 | X-CB 005 01 | 7a | LOGIC SOLVER | B10E-PS-SWITCH-01 | Red | 0.5mm² H05Z-K | 007/S7+ | PSU-B2 | 13 | DI2 | 0/1 | Moved
[5 empty] | DI7+ |  |  | 7b |  |  | Grey | 0.5mm² H05Z-K | 007/DI7+ | PSU-B2 | 14
B10E-PS-PSU-01:B3FAULT | 24VDC PSU B3 Fault | 24Vdc | 007 | 8 | S8+ | X-DI 32 05 | X-CB 005 01 | 8a | LOGIC SOLVER | B10E-PS-WLT-01 | Red | 0.5mm² H05Z-K | 007/S8+ | PSU-B3 | 13 | DI2 | 0/1 | Add
[5 empty] | DI8+ |  |  | 8b |  |  | Grey | 0.5mm² H05Z-K | 007/DI8+ | PSU-B3 | 14
B10E-PS-SWFLT-01 | Network Switch Fault | 24Vdc | 007 | 9 | S9+ | X-DI 32 05 | X-CB 005 01 | 9a | LOGIC SOLVER | B10E-PS-SWITCH-01 | Red | 0.5mm² H05Z-K | 007/S9+ | SWITCH1 | FAULT1 | DI2 | 0/1 | Moved
[5 empty] | DI9+ |  |  | 9b |  |  | Grey | 0.5mm² H05Z-K | 007/DI9+ | SWITCH1 | FAULT2
B10E-PS-WLT-01 | White Lights Enable (Relay Feedback) | 24Vdc | 007 | 10 | S10+ | X-DI 32 05 | X-CB 005 01 | 10a | LOGIC SOLVER | B10E-PS-WLT-01 | Red | 0.5mm² H05Z-K | 007/S10+ | CON-1 | 21 | DI2 | 0/1 | Moved
[5 empty] | DI10+ |  |  | 10b |  |  | Grey | 0.5mm² H05Z-K | 007/DI10+ | CON-1 | 22
B10E-PS-IOC-01:BOB:RESET | SIS Control Room Reset - CH1 - Beam Off Buttons | 24Vdc | 007 | 11 | S11+ | X-DI 32 05 | X-CB 005 01 | 11a | CCR | B10E-PS-INTF-08 | Red | 0.5mm² H05Z-K | 007/S11+ | X-INTF08 | 1 | DI1 | 0
[5 empty] | DI11+ |  |  | 11b |  |  | Grey | 0.5mm² H05Z-K | 007/DI11+ | X-INTF08 | 2
B10E-PS-IOC-01:SYS:RESET | SIS Control Room Reset - CH2 - System | 24Vdc | 007 | 12 | S12+ | X-DI 32 05 | X-CB 005 01 | 12a | CCR | B10E-PS-INTF-08 | Red | 0.5mm² H05Z-K | 007/S12+ | X-INTF08 | 3 | DI1 | 0
[5 empty] | DI12+ |  |  | 12b |  |  | Grey | 0.5mm² H05Z-K | 007/DI12+ | X-INTF08 | 4
B10E-PS-IOC-01:RDMN:RESET | SIS Control Room Reset - CH3 - RadMon | 24Vdc | 007 | 13 | S13+ | X-DI 32 05 | X-CB 005 01 | 13a | CCR | B10E-PS-INTF-08 | Red | 0.5mm² H05Z-K | 007/S13+ | X-INTF08 | 5 | DI1 | 0
[5 empty] | DI13+ |  |  | 13b |  |  | Grey | 0.5mm² H05Z-K | 007/DI13+ | X-INTF08 | 6
B10E-PS-IOC-01:GAS:RESET | SIS Control Room Reset - CH4 - Gas / O2 | 24Vdc | 007 | 14 | S14+ | X-DI 32 05 | X-CB 005 01 | 14a | CCR | B10E-PS-INTF-08 | Red | 0.5mm² H05Z-K | 007/S14+ | X-INTF08 | 7 | DI1 | 0
[5 empty] | DI14+ |  |  | 14b |  |  | Grey | 0.5mm² H05Z-K | 007/DI14+ | X-INTF08 | 8
B10E-PS-KEY-03 | Beamline Enable Key - Rack (Electron Source Enable/Disable) | 24Vdc | 007 | 15 | S15+ | X-DI 32 05 | X-CB 005 01 | 15a | LOCAL CONTROL ROOM | B10E-PS-KEY-03 | Red | 0.5mm² H05Z-K | 007/S15+ | X-KEY | 1 | DI1 | 0
[5 empty] | DI15+ |  |  | 15b |  |  | Grey | 0.5mm² H05Z-K | 007/DI15+ | X-KEY | 2
B10E-PS-KEY-02 | Hutch Enable Key (Interlocks Chicane Doors) | 24Vdc | 007 | 16 | S16+ | X-DI 32 05 | X-CB 005 01 | 16a | ZCP | B10E-PS-PKP-01 | Red | 0.5mm² H05Z-K | 007/S16+ | X-ZCP | 7 | DI1 | 0
[5 empty] | DI16+ |  |  | 16b |  |  | Grey | 0.5mm² H05Z-K | 007/DI16+ | X-ZCP | 8
B10E-PS-KEY-01 | Beamline Enable Key - ZCP (Electron Source Enable/Disable) | 24Vdc | 007 | 17 | S17+ | X-DI 32 05 | X-CB 005 01 | 17a | ZCP | B10E-PS-PKPE-01 | Red | 0.5mm² H05Z-K | 007/S17+ | X-ZCP | 3 | DI1 | 0
[5 empty] | DI17+ |  |  | 17b |  |  | Grey | 0.5mm² H05Z-K | 007/DI17+ | X-ZCP | 4
B10E-PS-SCR-01 | Search Card Reader | 24Vdc | 007 | 18 | S18+ | X-DI 32 05 | X-CB 005 01 | 18a | ZCP | B10E-PS-SCR-01 | Red | 0.5mm² H05Z-K | 007/S18+ | X-ZCP | 31 | DI1 | 0
[5 empty] | DI18+ |  |  | 18b |  |  | Grey | 0.5mm² H05Z-K | 007/DI18+ | X-ZCP | 32
B10E-PS-ASBF-01 | Area Search Button Final | 24Vdc | 007 | 19 | S19+ | X-DI 32 05 | X-CB 005 01 | 19a | ZCP | B10E-PS-ASBF-01 | Red | 0.5mm² H05Z-K | 007/S19+ | X-ZCP | 9 | DI1 | 0
[5 empty] | DI19+ |  |  | 19b |  |  | Grey | 0.5mm² H05Z-K | 007/DI19+ | X-ZCP | 10
B10E-PS-OR-01 | Open / Reset Pushbutton | 24Vdc | 007 | 20 | S20+ | X-DI 32 05 | X-CB 005 01 | 20a | ZCP | B10E-PS-OR-01 | Red | 0.5mm² H05Z-K | 007/S20+ | X-ZCP | 13 | DI1 | 0
[5 empty] | DI20+ |  |  | 20b |  |  | Grey | 0.5mm² H05Z-K | 007/DI20+ | X-ZCP | 14
B10E-PS-BLT-01 | Blue Light Test Switch (3 Position Switch - #1) | 24Vdc | 007 | 21 | S21+ | X-DI 32 05 | X-CB 005 01 | 21a | ZCP | B10E-PS-BLLCT-01 | Red | 0.5mm² H05Z-K | 007/S21+ | X-ZCP | 21 | DI1 | 0
[5 empty] | DI21+ |  |  | 21b |  |  | Grey | 0.5mm² H05Z-K | 007/DI21+ | X-ZCP | 22
B10E-PS-LCT-01 | Light Curtain Test Switch (3 Position Switch - #2) | 24Vdc | 007 | 22 | S22+ | X-DI 32 05 | X-CB 005 01 | 22a | ZCP | B10E-PS-BLLCT-01 | Red | 0.5mm² H05Z-K | 007/S22+ | X-ZCP | 23 | DI1 | 0
[5 empty] | DI22+ |  |  | 22b |  |  | Grey | 0.5mm² H05Z-K | 007/DI22+ | X-ZCP | 24
B10E-PS-WLON-01 | White Lights Enable Switch (Momentary Pushbutton) | 24Vdc | 007 | 23 | S23+ | X-DI 32 05 | X-CB 005 01 | 23a | ZCP | B10E-PS-WLON-01 | Red | 0.5mm² H05Z-K | 007/S23+ | X-ZCP | 25 | DI1 | 0
[5 empty] | DI23+ |  |  | 23b |  |  | Grey | 0.5mm² H05Z-K | 007/DI23+ | X-ZCP | 26
B10E-PS-LCRx-01 | Light Curtain Receiver 01 | 24Vdc | 007 | 24 | S24+ | X-DI 32 05 | X-CB 005 01 | 24a | EXTERNAL (VIA ZCP) | B10E-PS-LCRx-01 | Red | 0.5mm² H05Z-K | 007/S24+ | X-ZCP | 37 | DI1 | 0
[5 empty] | DI24+ |  |  | 24b |  |  | Grey | 0.5mm² H05Z-K | 007/DI24+ | X-ZCP | 38
B10E-PS-CON-01:FB | Power Contactor 01 Feedback | 24Vdc | 007 | 25 | S25+ | X-DI 32 05 | X-CB 005 01 | 25a | ELECTRON SOURCE | B10E-PS-CON-01 | Red | 0.5mm² H05Z-K | 007/S25+ | X-INTF07 | 3 | DI1 | 0
[5 empty] | DI25+ |  |  | 25b |  |  | Grey | 0.5mm² H05Z-K | 007/DI25+ | X-INTF07 | 4
B10E-PS-CON-02:FB | Power Contactor 02 Feedback | 24Vdc | 007 | 26 | S26+ | X-DI 32 05 | X-CB 005 01 | 26a | ELECTRON SOURCE | B10E-PS-CON-02 | Red | 0.5mm² H05Z-K | 007/S26+ | X-INTF07 | 7 | DI1 | 0
[5 empty] | DI26+ |  |  | 26b |  |  | Grey | 0.5mm² H05Z-K | 007/DI26+ | X-INTF07 | 8
B10E-PS-CON-03:FB | Power Contactor 03 Feedback | 24Vdc | 007 | 27 | S27+ | X-DI 32 05 | X-CB 005 01 | 27a | ELECTRON SOURCE | B10E-PS-CON-03 | Red | 0.5mm² H05Z-K | 007/S27+ | X-INTF07 | 11 | DI1 | 0
[5 empty] | DI27+ |  |  | 27b |  |  | Grey | 0.5mm² H05Z-K | 007/DI27+ | X-INTF07 | 12
B10E-PS-CON-04:FB | Power Contactor 04 Feedback | 24Vdc | 007 | 28 | S28+ | X-DI 32 05 | X-CB 005 01 | 28a | ELECTRON SOURCE | B10E-PS-CON-04 | Red | 0.5mm² H05Z-K | 007/S28+ | X-INTF07 | 15 | DI1 | 0
[5 empty] | DI28+ |  |  | 28b |  |  | Grey | 0.5mm² H05Z-K | 007/DI28+ | X-INTF07 | 16
B10E-PS-CON-05:FB | Power Contactor 05 Feedback | 24Vdc | 007 | 29 | S29+ | X-DI 32 05 | X-CB 005 01 | 29a | ELECTRON SOURCE | B10E-PS-CON-05 | Red | 0.5mm² H05Z-K | 007/S29+ | X-INTF07 | 19 | DI1 | 0
[5 empty] | DI29+ |  |  | 29b |  |  | Grey | 0.5mm² H05Z-K | 007/DI29+ | X-INTF07 | 20
B10E-PS-GADC-03 | General Access Door Closed Position Switch 3 (N/O when Door Open) | 24Vdc | 007 | 30 | S30+ | X-DI 32 05 | X-CB 005 01 | 30a | HUTCH | B10E-PS-DS-03 | Red | 0.5mm² H05Z-K | 007/S30+ | X-DS03 | 1 | DI1 | 0
[5 empty] | DI30+ |  |  | 30b |  |  | Grey | 0.5mm² H05Z-K | 007/DI30+ | X-DS03 | 2
B10E-PS-GADC-06 | General Access Gate Closed Position Switch 3 (N/O when Gate Open) | 24Vdc | 007 | 31 | S31+ | X-DI 32 05 | X-CB 005 01 | 31a | EXTERNAL | B10E-PS-DS-06 | Red | 0.5mm² H05Z-K | 007/S31+ | X-DS06 | 1 | DI1 | 0
[5 empty] | DI31+ |  |  | 31b |  |  | Grey | 0.5mm² H05Z-K | 007/DI31+ | X-DS06 | 2
B10E-PS-SADC-03 | Service Access Door Closed Position Switch 3 (N/O when Door Open) | 24Vdc | 007 | 32 | S32+ | X-DI 32 05 | X-CB 005 01 | 32a | HUTCH | B10E-PS-DS-09 | Red | 0.5mm² H05Z-K | 007/S32+ | X-DS09 | 1 | DI1 | 0
[5 empty] | DI32+ |  |  | 32b |  |  | Grey | 0.5mm² H05Z-K | 007/DI32+ | X-DS09 | 2

## 008_DI
TAG | DESCRIPTION | SIGNAL TYPE | CHASSIS &SLOT No | Channel. No. | Signal | MODULE | CONNECTION BOARD | CB TERM. | DEVICE LOCATION | DEVICE TAG | WIRE COLOUR | WIRE TYPE | WIRE NUMBER | TERMINAL BLOCK | TERM. No. | Loop Type | REV.
B10E-PS-GADC-01 | General Access Door Closed Position Switch 1 (N/O when Door Open) | 24Vdc | 008 | 1 | S1+ | X-DI 32 05 | X-CB 005 01 | 1a | EXTERNAL | B10E-PS-DS-01 | Red | 0.5mm² H05Z-K | 008/S1+ | X-DS01 | 3 | DI1 | 0
[5 empty] | DI1+ |  |  | 1b |  |  | Grey | 0.5mm² H05Z-K | 008/DI1+ | X-DS01 | 4
B10E-PS-GADL-01 | General Access Door Locked Position Switch 1 | 24Vdc | 008 | 2 | S2+ | X-DI 32 05 | X-CB 005 01 | 2a | EXTERNAL | B10E-PS-DS-01 | Red | 0.5mm² H05Z-K | 008/S2+ | X-DS01 | 5 | DI1 | 0
[5 empty] | DI2+ |  |  | 2b |  |  | Grey | 0.5mm² H05Z-K | 008/DI2+ | X-DS01 | 6
SPDI-008/3 | Wired Spare Input (Reserved) | 24Vdc | 008 | 3 | S3+ | X-DI 32 05 | X-CB 005 01 | 3a | HUTCH | B10E-PS-DS-03 | Red | 0.5mm² H05Z-K | 008/S3+ | X-DS03 | 3 | DI1 | 0
[5 empty] | DI3+ |  |  | 3b |  |  | Grey | 0.5mm² H05Z-K | 008/DI3+ | X-DS03 | 4
B10E-PS-GADC-04 | General Access Gate Closed Position Switch 1 (N/O when Gate Open) | 24Vdc | 008 | 4 | S4+ | X-DI 32 05 | X-CB 005 01 | 4a | EXTERNAL | B10E-PS-DS-04 | Red | 0.5mm² H05Z-K | 008/S4+ | X-DS04 | 3 | DI1 | 0
[5 empty] | DI4+ |  |  | 4b |  |  | Grey | 0.5mm² H05Z-K | 008/DI4+ | X-DS04 | 4
B10E-PS-GADL-04 | General Access Gate Locked Position Switch 1 | 24Vdc | 008 | 5 | S5+ | X-DI 32 05 | X-CB 005 01 | 5a | EXTERNAL | B10E-PS-DS-04 | Red | 0.5mm² H05Z-K | 008/S5+ | X-DS04 | 5 | DI1 | 0
[5 empty] | DI5+ |  |  | 5b |  |  | Grey | 0.5mm² H05Z-K | 008/DI5+ | X-DS04 | 6
SPDI-008/6 | Wired Spare Input (Reserved) | 24Vdc | 008 | 6 | S6+ | X-DI 32 05 | X-CB 005 01 | 6a | EXTERNAL | B10E-PS-DS-06 | Red | 0.5mm² H05Z-K | 008/S6+ | X-DS06 | 3 | DI2 | 0/1
[5 empty] | DI6+ |  |  | 6b |  |  | Grey | 0.5mm² H05Z-K | 008/DI6+ | X-DS06 | 4
B10E-PS-SADC-01 | Service Access Door Closed Position Switch 1 (N/O when Door Open) | 24Vdc | 008 | 7 | S7+ | X-DI 32 05 | X-CB 005 01 | 7a | EXTERNAL | B10E-PS-DS-07 | Red | 0.5mm² H05Z-K | 008/S7+ | X-DS07 | 3 | DI1 | 0
[5 empty] | DI7+ |  |  | 7b |  |  | Grey | 0.5mm² H05Z-K | 008/DI7+ | X-DS07 | 4
B10E-PS-SADL-01 | Service Access Door Locked Position Switch 1 | 24Vdc | 008 | 8 | S8+ | X-DI 32 05 | X-CB 005 01 | 8a | EXTERNAL | B10E-PS-DS-07 | Red | 0.5mm² H05Z-K | 008/S8+ | X-DS07 | 5 | DI1 | 0
[5 empty] | DI8+ |  |  | 8b |  |  | Grey | 0.5mm² H05Z-K | 008/DI8+ | X-DS07 | 6
SPDI-008/9 | Wired Spare Input (Reserved) | 24Vdc | 008 | 9 | S9+ | X-DI 32 05 | X-CB 005 01 | 9a | HUTCH | B10E-PS-DS-09 | Red | 0.5mm² H05Z-K | 008/S9+ | X-DS09 | 3 | DI2 | 0/1
[5 empty] | DI9+ |  |  | 9b |  |  | Grey | 0.5mm² H05Z-K | 008/DI9+ | X-DS09 | 4
B10E-PS-SADC-04 | Service Access Door Closed Position Switch 4 (N/O when Door Open) | 24Vdc | 008 | 10 | S10+ | X-DI 32 05 | X-CB 005 01 | 10a | HUTCH | B10E-PS-DS-10 | Red | 0.5mm² H05Z-K | 008/S10+ | X-DS10 | 1 | DI1 | 0
[5 empty] | DI10+ |  |  | 10b |  |  | Grey | 0.5mm² H05Z-K | 008/DI10+ | X-DS10 | 2
SPDI-008/11 | Wired Spare Input (RESERVED) | 24Vdc | 008 | 11 | S11+ | X-DI 32 05 | X-CB 005 01 | 11a |  | B10E-PS-DS-10 | Red | 0.5mm² H05Z-K | 008/S11+ | X-DS10 | 3 | DI2 | 0/1
[5 empty] | DI11+ |  |  | 11b |  |  | Grey | 0.5mm² H05Z-K | 008/DI11+ | X-DS10 | 4
B10E-PS-KEY-04 | Software Download/Program Enable Keyswitch | 24Vdc | 008 | 12 | S12+ | X-DI 32 05 | X-CB 005 01 | 12a | LOGIC SOLVER | B10E-PS-KEY-04 | Red | 0.5mm² H05Z-K | 008/S12+ | KS-1 | 13 | DI2 | 0/1 |  | Changed
[5 empty] | DI12+ |  |  | 12b |  |  | Grey | 0.5mm² H05Z-K | 008/DI12+ | KS-1 | 23
B10E-PS-BOB-01:A | Beam Off Button 01 | 24Vdc | 008 | 13 | S13+ | X-DI 32 05 | X-CB 005 01 | 13a | ZCP | B10E-PS-BOB-01 | Red | 0.5mm² H05Z-K | 008/S13+ | X-ZCP | 17 | DI1 | 0
| 5 |  |  |  | DI13+ |  |  | 13b |  |  | Grey | 0.5mm² H05Z-K | 008/DI13+ | X-ZCP | 18
B10E-PS-BOB-02:A | Beam Off Button 02 | 24Vdc | 008 | 14 | S14+ | X-DI 32 05 | X-CB 005 01 | 14a | HUTCH | B10E-PS-BOB-02 | Red | 0.5mm² H05Z-K | 008/S14+ | X-BOB | 1 | DI1 | 0
[5 empty] | DI14+ |  |  | 14b |  |  | Grey | 0.5mm² H05Z-K | 008/DI14+ | X-BOB | 2
B10E-PS-BOB-03:A | Beam Off Button 03 | 24Vdc | 008 | 15 | S15+ | X-DI 32 05 | X-CB 005 01 | 15a | HUTCH | B10E-PS-BOB-03 | Red | 0.5mm² H05Z-K | 008/S15+ | X-BOB | 5 | DI1 | 0
[5 empty] | DI15+ |  |  | 15b |  |  | Grey | 0.5mm² H05Z-K | 008/DI15+ | X-BOB | 6
B10E-PS-BOB-04:A | Beam Off Button 04 | 24Vdc | 008 | 16 | S16+ | X-DI 32 05 | X-CB 005 01 | 16a | HUTCH | B10E-PS-BOB-04 | Red | 0.5mm² H05Z-K | 008/S16+ | X-BOB | 9 | DI1 | 0
[5 empty] | DI16+ |  |  | 16b |  |  | Grey | 0.5mm² H05Z-K | 008/DI16+ | X-BOB | 10
B10E-PS-BOB-05:A | Beam Off Button 05 | 24Vdc | 008 | 17 | S17+ | X-DI 32 05 | X-CB 005 01 | 17a | HUTCH | B10E-PS-BOB-05 | Red | 0.5mm² H05Z-K | 008/S17+ | X-BOB | 13 | DI1 | 0
[5 empty] | DI17+ |  |  | 17b |  |  | Grey | 0.5mm² H05Z-K | 008/DI17+ | X-BOB | 14
B10E-PS-BOB-06:A | Beam Off Button 06 | 24Vdc | 008 | 18 | S18+ | X-DI 32 05 | X-CB 005 01 | 18a | HUTCH | B10E-PS-BOB-06 | Red | 0.5mm² H05Z-K | 008/S18+ | X-BOB | 17 | DI1 | 0
[5 empty] | DI18+ |  |  | 18b |  |  | Grey | 0.5mm² H05Z-K | 008/DI18+ | X-BOB | 18
B10E-PS-BOB-07:A | Beam Off Button 07 | 24Vdc | 008 | 19 | S19+ | X-DI 32 05 | X-CB 005 01 | 19a | HUTCH | B10E-PS-BOB-07 | Red | 0.5mm² H05Z-K | 008/S19+ | X-BOB | 21 | DI1 | 0
[5 empty] | DI19+ |  |  | 19b |  |  | Grey | 0.5mm² H05Z-K | 008/DI19+ | X-BOB | 22
B10E-PS-BOB-08:A | Beam Off Button 08 | 24Vdc | 008 | 20 | S20+ | X-DI 32 05 | X-CB 005 01 | 20a | HUTCH | B10E-PS-BOB-08 | Red | 0.5mm² H05Z-K | 008/S20+ | X-BOB | 25 | DI1 | 0
[5 empty] | DI20+ |  |  | 20b |  |  | Grey | 0.5mm² H05Z-K | 008/DI20+ | X-BOB | 26
SPDI-008/21 | Wired Spare Input | 24Vdc | 008 | 21 | S21+ | X-DI 32 05 | X-CB 005 01 | 21a |  |  | Red | 0.5mm² H05Z-K | 008/S21+ | X-SPDI | 1 | DI2 | 0/1 |  | Change term
[5 empty] | DI21+ |  |  | 21b |  |  | Grey | 0.5mm² H05Z-K | 008/DI21+ | X-SPDI | 2
SPDI-008/22 | Wired Spare Input | 24Vdc | 008 | 22 | S22+ | X-DI 32 05 | X-CB 005 01 | 22a |  |  | Red | 0.5mm² H05Z-K | 008/S22+ | X-SPDI | 3 | DI2 | 0/1 |  | Change term
[5 empty] | DI22+ |  |  | 22b |  |  | Grey | 0.5mm² H05Z-K | 008/DI22+ | X-SPDI | 4
B10E-PS-ASB-01 | Area Search Button 01 | 24Vdc | 008 | 23 | S23+ | X-DI 32 05 | X-CB 005 01 | 23a | HUTCH | B10E-PS-ASB-01 | Red | 0.5mm² H05Z-K | 008/S23+ | X-ASB | 1 | DI1 | 0
[5 empty] | DI23+ |  |  | 23b |  |  | Grey | 0.5mm² H05Z-K | 008/DI23+ | X-ASB | 2
B10E-PS-ASB-02 | Area Search Button 02 | 24Vdc | 008 | 24 | S24+ | X-DI 32 05 | X-CB 005 01 | 24a | HUTCH | B10E-PS-ASB-02 | Red | 0.5mm² H05Z-K | 008/S24+ | X-ASB | 5 | DI1 | 0
[5 empty] | DI24+ |  |  | 24b |  |  | Grey | 0.5mm² H05Z-K | 008/DI24+ | X-ASB | 6
B10E-PS-ASB-03 | Area Search Button 03 | 24Vdc | 008 | 25 | S25+ | X-DI 32 05 | X-CB 005 01 | 25a | HUTCH | B10E-PS-ASB-03 | Red | 0.5mm² H05Z-K | 008/S25+ | X-ASB | 9 | DI1 | 0
[5 empty] | DI25+ |  |  | 25b |  |  | Grey | 0.5mm² H05Z-K | 008/DI25+ | X-ASB | 10
B10E-PS-ASB-04 | Area Search Button 04 | 24Vdc | 008 | 26 | S26+ | X-DI 32 05 | X-CB 005 01 | 26a | HUTCH | B10E-PS-ASB-04 | Red | 0.5mm² H05Z-K | 008/S26+ | X-ASB | 13 | DI1 | 0
[5 empty] | DI26+ |  |  | 26b |  |  | Grey | 0.5mm² H05Z-K | 008/DI26+ | X-ASB | 14
B10E-PS-UPS-01 | UPS Feedback 01 | 24Vdc | 008 | 27 | S27+ | X-DI 32 05 | X-CB 005 01 | 27a |  |  | Red | 0.5mm² H05Z-K | 008/S27+ | X-UPS | 1 | DI1 | 0/1 | Added
[5 empty] | DI27+ |  |  | 27b |  |  | Grey | 0.5mm² H05Z-K | 008/DI27+ | X-UPS | 2
B10E-PS-UPS-02 | UPS Feedback 02 | 24Vdc | 008 | 28 | S28+ | X-DI 32 05 | X-CB 005 01 | 28a |  |  | Red | 0.5mm² H05Z-K | 008/S28+ | X-UPS | 3 | DI1 | 0/1 | Added
[5 empty] | DI28+ |  |  | 28b |  |  | Grey | 0.5mm² H05Z-K | 008/DI28+ | X-UPS | 4
SPDI-008/29 | Wired Spare Input | 24Vdc | 008 | 29 | S29+ | X-DI 32 05 | X-CB 005 01 | 29a |  |  | Red | 0.5mm² H05Z-K | 008/S29+ | X-SPDI | 5 | DI2 | 0/1 |  | Change term
[5 empty] | DI29+ |  |  | 29b |  |  | Grey | 0.5mm² H05Z-K | 008/DI29+ | X-SPDI | 6
SPDI-008/30 | Wired Spare Input | 24Vdc | 008 | 30 | S30+ | X-DI 32 05 | X-CB 005 01 | 30a |  |  | Red | 0.5mm² H05Z-K | 008/S30+ | X-SPDI | 7 | DI2 | 0/1 |  | Change term
[5 empty] | DI30+ |  |  | 30b |  |  | Grey | 0.5mm² H05Z-K | 008/DI30+ | X-SPDI | 8
SPDI-008/31 | Wired Spare Input | 24Vdc | 008 | 31 | S31+ | X-DI 32 05 | X-CB 005 01 | 31a |  |  | Red | 0.5mm² H05Z-K | 008/S31+ | X-SPDI | 9 | DI2 | 0/1 |  | Change term
[5 empty] | DI31+ |  |  | 31b |  |  | Grey | 0.5mm² H05Z-K | 008/DI31+ | X-SPDI | 10
SPDI-008/32 | Wired Spare Input | 24Vdc | 008 | 32 | S32+ | X-DI 32 05 | X-CB 005 01 | 32a |  |  | Red | 0.5mm² H05Z-K | 008/S32+ | X-SPDI | 11 | DI2 | 0/1 |  | Change term
[5 empty] | DI32+ |  |  | 32b |  |  | Grey | 0.5mm² H05Z-K | 008/DI32+ | X-SPDI | 12

## 009_DI
TAG | DESCRIPTION | SIGNAL TYPE | CHASSIS &SLOT No | Channel. No. | Signal | MODULE | CONNECTION BOARD | CB TERM. | DEVICE LOCATION | DEVICE TAG | WIRE COLOUR | WIRE TYPE | WIRE NUMBER | TERMINAL BLOCK | TERM. No. | Loop Type | REV.
B10E-PS-GADC-02 | General Access Door Closed Position Switch 2 (N/O when Door Open) | 24Vdc | 009 | 1 | S1+ | X-DI 32 05 | X-CB 005 01 | 1a | EXTERNAL | B10E-PS-DS-02 | Red | 0.5mm² H05Z-K | 009/S1+ | X-DS02 | 3 | DI1 | 0
[5 empty] | DI1+ |  |  | 1b |  |  | Grey | 0.5mm² H05Z-K | 009/DI1+ | X-DS02 | 4
B10E-PS-GADL-02 | General Access Door Locked Position Switch 2 | 24Vdc | 009 | 2 | S2+ | X-DI 32 05 | X-CB 005 01 | 2a | EXTERNAL | B10E-PS-DS-02 | Red | 0.5mm² H05Z-K | 009/S2+ | X-DS02 | 5 | DI1 | 0
[5 empty] | DI2+ |  |  | 2b |  |  | Grey | 0.5mm² H05Z-K | 009/DI2+ | X-DS02 | 6
SPDI-009/3 | Wired Spare Input | 24Vdc | 009 | 3 | S3+ | X-DI 32 05 | X-CB 005 01 | 3a |  |  | Red | 0.5mm² H05Z-K | 009/S3+ | X-SPDI | 13 | DI2 | 0/1 | change term
[5 empty] | DI3+ |  |  | 3b |  |  | Grey | 0.5mm² H05Z-K | 009/DI3+ | X-SPDI | 14
B10E-PS-GADC-05 | General Access Gate Closed Position Switch 2 (N/O when Gate Open) | 24Vdc | 009 | 4 | S4+ | X-DI 32 05 | X-CB 005 01 | 4a | EXTERNAL | B10E-PS-DS-05 | Red | 0.5mm² H05Z-K | 009/S4+ | X-DS05 | 3 | DI1 | 0
[5 empty] | DI4+ |  |  | 4b |  |  | Grey | 0.5mm² H05Z-K | 009/DI4+ | X-DS05 | 4
B10E-PS-GADL-05 | General Access Gate Locked Position Switch 1 | 24Vdc | 009 | 5 | S5+ | X-DI 32 05 | X-CB 005 01 | 5a | EXTERNAL | B10E-PS-DS-05 | Red | 0.5mm² H05Z-K | 009/S5+ | X-DS05 | 5 | DI1 | 0
[5 empty] | DI5+ |  |  | 5b |  |  | Grey | 0.5mm² H05Z-K | 009/DI5+ | X-DS05 | 6
SPDI-009/6 | Wired Spare Input | 24Vdc | 009 | 6 | S6+ | X-DI 32 05 | X-CB 005 01 | 6a |  |  | Red | 0.5mm² H05Z-K | 009/S6+ | X-SPDI | 15 | DI2 | 0/1 | term change
[5 empty] | DI6+ |  |  | 6b |  |  | Grey | 0.5mm² H05Z-K | 009/DI6+ | X-SPDI | 16
B10E-PS-SADC-02 | Service Access Door Closed Position Switch 2 (N/O when Door Open) | 24Vdc | 009 | 7 | S7+ | X-DI 32 05 | X-CB 005 01 | 7a | EXTERNAL | B10E-PS-DS-08 | Red | 0.5mm² H05Z-K | 009/S7+ | X-DS08 | 3 | DI1 | 0
[5 empty] | DI7+ |  |  | 7b |  |  | Grey | 0.5mm² H05Z-K | 009/DI7+ | X-DS08 | 4
B10E-PS-SADL-02 | Service Access Door Locked Position Switch 2 | 24Vdc | 009 | 8 | S8+ | X-DI 32 05 | X-CB 005 01 | 8a | EXTERNAL | B10E-PS-DS-08 | Red | 0.5mm² H05Z-K | 009/S8+ | X-DS08 | 5 | DI1 | 0
[5 empty] | DI8+ |  |  | 8b |  |  | Grey | 0.5mm² H05Z-K | 009/DI8+ | X-DS08 | 6
SPDI-009/9 | Wired Spare Input (RESERVED) | 24Vdc | 009 | 9 | S9+ | X-DI 32 05 | X-CB 005 01 | 9a |  | B10E-PS-DS-09 | Red | 0.5mm² H05Z-K | 009/S9+ | X-SPDI | 17 | DI2 | 0/1 | term change
[5 empty] | DI9+ |  |  | 9b |  |  | Grey | 0.5mm² H05Z-K | 009/DI9+ | X-SPDI | 18
B10E-PS-SADC-05 | Service Access Door Closed Position Switch 5 (N/O when Door Open) | 24Vdc | 009 | 10 | S10+ | X-DI 32 05 | X-CB 005 01 | 10a | HUTCH | B10E-PS-DS-11 | Red | 0.5mm² H05Z-K | 009/S10+ | X-DS11 | 1 | DI1 | 0
[5 empty] | DI10+ |  |  | 10b |  |  | Grey | 0.5mm² H05Z-K | 009/DI10+ | X-DS11 | 2
SPDI-009/11 | Wired Spare Input (RESERVED) | 24Vdc | 009 | 11 | S11+ | X-DI 32 05 | X-CB 005 01 | 11a |  | B10E-PS-DS-11 | Red | 0.5mm² H05Z-K | 009/S11+ | X-DS11 | 3 | DI2 | 0/1
[5 empty] | DI11+ |  |  | 11b |  |  | Grey | 0.5mm² H05Z-K | 009/DI11+ | X-DS11 | 4
SPDI-009/12 | Wired Spare Input | 24Vdc | 009 | 12 | S12+ | X-DI 32 05 | X-CB 005 01 | 12a | HUTCH | B10E-PS-DS-12 | Red | 0.5mm² H05Z-K | 009/S12+ | X-SPDI | 19 | DI2 | 0/1 | Removed
[5 empty] | DI12+ |  |  | 12b |  |  | Grey | 0.5mm² H05Z-K | 009/DI12+ | X-SPDI | 20 |  |  | change to spare
B10E-PS-BOB-01:B | Beam Off Button 01 | 24Vdc | 009 | 13 | S13+ | X-DI 32 05 | X-CB 005 01 | 13a | ZCP | B10E-PS-BOB-01 | Red | 0.5mm² H05Z-K | 009/S13+ | X-ZCP | 19 | DI1 | 0
[5 empty] | DI13+ |  |  | 13b |  |  | Grey | 0.5mm² H05Z-K | 009/DI13+ | X-ZCP | 20
B10E-PS-BOB-02:B | Beam Off Button 02 | 24Vdc | 009 | 14 | S14+ | X-DI 32 05 | X-CB 005 01 | 14a | HUTCH | B10E-PS-BOB-02 | Red | 0.5mm² H05Z-K | 009/S14+ | X-BOB | 3 | DI1 | 0
[5 empty] | DI14+ |  |  | 14b |  |  | Grey | 0.5mm² H05Z-K | 009/DI14+ | X-BOB | 4
B10E-PS-BOB-03:B | Beam Off Button 03 | 24Vdc | 009 | 15 | S15+ | X-DI 32 05 | X-CB 005 01 | 15a | HUTCH | B10E-PS-BOB-03 | Red | 0.5mm² H05Z-K | 009/S15+ | X-BOB | 7 | DI1 | 0
[5 empty] | DI15+ |  |  | 15b |  |  | Grey | 0.5mm² H05Z-K | 009/DI15+ | X-BOB | 8
B10E-PS-BOB-04:B | Beam Off Button 04 | 24Vdc | 009 | 16 | S16+ | X-DI 32 05 | X-CB 005 01 | 16a | HUTCH | B10E-PS-BOB-04 | Red | 0.5mm² H05Z-K | 009/S16+ | X-BOB | 11 | DI1 | 0
[5 empty] | DI16+ |  |  | 16b |  |  | Grey | 0.5mm² H05Z-K | 009/DI16+ | X-BOB | 12
B10E-PS-BOB-05:B | Beam Off Button 05 | 24Vdc | 009 | 17 | S17+ | X-DI 32 05 | X-CB 005 01 | 17a | HUTCH | B10E-PS-BOB-05 | Red | 0.5mm² H05Z-K | 009/S17+ | X-BOB | 15 | DI1 | 0
[5 empty] | DI17+ |  |  | 17b |  |  | Grey | 0.5mm² H05Z-K | 009/DI17+ | X-BOB | 16
B10E-PS-BOB-06:B | Beam Off Button 06 | 24Vdc | 009 | 18 | S18+ | X-DI 32 05 | X-CB 005 01 | 18a | HUTCH | B10E-PS-BOB-06 | Red | 0.5mm² H05Z-K | 009/S18+ | X-BOB | 19 | DI1 | 0
[5 empty] | DI18+ |  |  | 18b |  |  | Grey | 0.5mm² H05Z-K | 009/DI18+ | X-BOB | 20
B10E-PS-BOB-07:B | Beam Off Button 07 | 24Vdc | 009 | 19 | S19+ | X-DI 32 05 | X-CB 005 01 | 19a | HUTCH | B10E-PS-BOB-07 | Red | 0.5mm² H05Z-K | 009/S19+ | X-BOB | 23 | DI1 | 0
[5 empty] | DI19+ |  |  | 19b |  |  | Grey | 0.5mm² H05Z-K | 009/DI19+ | X-BOB | 24
B10E-PS-BOB-08:B | Beam Off Button 08 | 24Vdc | 009 | 20 | S20+ | X-DI 32 05 | X-CB 005 01 | 20a | HUTCH | B10E-PS-BOB-08 | Red | 0.5mm² H05Z-K | 009/S20+ | X-BOB | 27 | DI1 | 0
[5 empty] | DI20+ |  |  | 20b |  |  | Grey | 0.5mm² H05Z-K | 009/DI20+ | X-BOB | 28
B10E-PS-SOVLN2-01:OP | Liquid Nitrogen Shuttoff Valve OPEN | 24Vdc | 009 | 21 | S21+ | X-DI 32 05 | X-CB 005 01 | 21a | EXTERNAL | B10E-PS-SOVLN2-01 | Red | 0.5mm² H05Z-K | 009/S21+ | X-SOVLN2 | 3 | DI1 | 0
[5 empty] | DI21+ |  |  | 21b |  |  | Grey | 0.5mm² H05Z-K | 009/DI21+ | X-SOVLN2 | 4
B10E-PS-SOVLN2-01:CL | Liquid Nitrogen Shuttoff Valve CLOSED | 24Vdc | 009 | 22 | S22+ | X-DI 32 05 | X-CB 005 01 | 22a | EXTERNAL | B10E-PS-SOVLN2-01 | Red | 0.5mm² H05Z-K | 009/S22+ | X-SOVLN2 | 5 | DI1 | 0
[5 empty] | DI22+ |  |  | 22b |  |  | Grey | 0.5mm² H05Z-K | 009/DI22+ | X-SOVLN2 | 6
B10E-PS-RDMND-01 | Radiation Monitor 01 | 24Vdc | 009 | 23 | S23+ | X-DI 32 05 | X-CB 005 01 | 23a | EXTERNAL | B10E-PS-RADMN-01 | Red | 0.5mm² H05Z-K | 009/S23+ | X-RADMN | 1 | DI1 | 0
[5 empty] | DI23+ |  |  | 23b |  |  | Grey | 0.5mm² H05Z-K | 009/DI23+ | X-RADMN | 2
B10E-PS-RDMNR-01 | Radiation Monitor 01 | 24Vdc | 009 | 24 | S24+ | X-DI 32 05 | X-CB 005 01 | 24a | EXTERNAL | B10E-PS-RADMN-01 | Red | 0.5mm² H05Z-K | 009/S24+ | X-RADMN | 3 | DI1 | 0
[5 empty] | DI24+ |  |  | 24b |  |  | Grey | 0.5mm² H05Z-K | 009/DI24+ | X-RADMN | 4
B10E-PS-RDMND-02 | Radiation Monitor 02 | 24Vdc | 009 | 25 | S25+ | X-DI 32 05 | X-CB 005 01 | 25a | EXTERNAL | B10E-PS-RADMN-02 | Red | 0.5mm² H05Z-K | 009/S25+ | X-RADMN | 5 | DI1 | 0
[5 empty] | DI25+ |  |  | 25b |  |  | Grey | 0.5mm² H05Z-K | 009/DI25+ | X-RADMN | 6
B10E-PS-RDMNR-02 | Radiation Monitor 02 | 24Vdc | 009 | 26 | S26+ | X-DI 32 05 | X-CB 005 01 | 26a | EXTERNAL | B10E-PS-RADMN-02 | Red | 0.5mm² H05Z-K | 009/S26+ | X-RADMN | 7 | DI1 | 0
[5 empty] | DI26+ |  |  | 26b |  |  | Grey | 0.5mm² H05Z-K | 009/DI26+ | X-RADMN | 8
B10E-PS-CON-06:FB | Power Contactor 06 Feedback (3 Phase RF Power) | 24Vdc | 009 | 27 | S27+ | X-DI 32 05 | X-CB 005 01 | 27a | ELECTRON SOURCE | B10E-PS-CON-06 | Red | 0.5mm² H05Z-K | 009/S27+ | X-INTF07 | 45 | DI1 | 0/2 | New DI
[5 empty] | DI27+ |  |  | 27b |  |  | Grey | 0.5mm² H05Z-K | 009/DI27+ | X-INTF07 | 46
B10E-PS-CON-07:FB | Power Contactor 07 Feedback (3 Phase RF Power) | 24Vdc | 009 | 28 | S28+ | X-DI 32 05 | X-CB 005 01 | 28a | ELECTRON SOURCE | B10E-PS-CON-07 | Red | 0.5mm² H05Z-K | 009/S28+ | X-INTF07 | 49 | DI1 | 0/2 | New DI
[5 empty] | DI28+ |  |  | 28b |  |  | Grey | 0.5mm² H05Z-K | 009/DI28+ | X-INTF07 | 50
B10E-PS-CON-08:FB | Power Contactor 08 Feedback (3 Phase RF Power) | 24Vdc | 009 | 29 | S29+ | X-DI 32 05 | X-CB 005 01 | 29a | ELECTRON SOURCE | B10E-PS-CON-08 | Red | 0.5mm² H05Z-K | 009/S29+ | X-INTF07 | 53 | DI1 | 0/2 | New DI
[5 empty] | DI29+ |  |  | 29b |  |  | Grey | 0.5mm² H05Z-K | 009/DI29+ | X-INTF07 | 54
B10E-PS-CON-09:FB | Power Contactor 09 Feedback (1 Phase RF Drive) | 24Vdc | 009 | 30 | S30+ | X-DI 32 05 | X-CB 005 01 | 30a | ELECTRON SOURCE | B10E-PS-CON-09 | Red | 0.5mm² H05Z-K | 009/S30+ | X-INTF07 | 57 | DI1 | 0/2 | New DI
[5 empty] | DI30+ |  |  | 30b |  |  | Grey | 0.5mm² H05Z-K | 009/DI30+ | X-INTF07 | 58
B10E-PS-CON-10:FB | Power Contactor 10 Feedback (1 Phase RF Drive) | 24Vdc | 009 | 31 | S31+ | X-DI 32 05 | X-CB 005 01 | 31a | ELECTRON SOURCE | B10E-PS-CON-10 | Red | 0.5mm² H05Z-K | 009/S31+ | X-INTF07 | 61 | DI1 | 0/2 | New DI
[5 empty] | DI31+ |  |  | 31b |  |  | Grey | 0.5mm² H05Z-K | 009/DI31+ | X-INTF07 | 62
SPDI-009/32 | Wired Spare Input | 24Vdc | 009 | 32 | S32+ | X-DI 32 05 | X-CB 005 01 | 32a |  |  | Red | 0.5mm² H05Z-K | 009/S32+ | X-SPDI | 31 | DI2 | 0/1
[5 empty] | DI32+ |  |  | 32b |  |  | Grey | 0.5mm² H05Z-K | 009/DI32+ | X-SPDI | 32

## 013_DO
TAG | DESCRIPTION | SIGNAL TYPE | CHASSIS &SLOT No | CHANNEL NO. | SIGNAL | MODULE | CONNECTION BOARD | CB TERM. | WIRE COLOUR | WIRE TYPE | WIRE NUMBER | DEVICE TERM. IN | DEVICE | DEVICE TERM. OUT | DEVICE LOCATION | DEVICE TAG | WIRE COLOUR | WIRE TYPE | WIRE NUMBER | TERMINAL BLOCK | TERM. No. | Loop Type | REV.
B10E-PS-WLT-01:EN | White Lights Enable (Relay) | 24Vdc | 013 | 1 | DO1+ | X-DO 24 01 | X-CB 009 01 | 1a | Grey | 0.75mm² H05Z-K | 013/DO1+ | A1 | CON-1 |  |  | B10E-PS-WLT-01 | [5 empty] | SEE | 0/1
[5 empty] | DO1- |  |  | 1b | White | 0.75mm² H05Z-K | 013/DO1- | A2 | [9 empty] | DWG 72
[5 empty] | 13L+ |  |  |  | Red | 2.5mm² H07Z-K | 13L+ | 1/L1 |  | 2/T1 |  |  | Red | 2.5mm² H07Z-K | CON1/:2 | X-WLT | 1 |  |  | Change wire size
[5 empty] | 14L+ |  |  |  | Red | 2.5mm² H07Z-K | 14L+ | 3/L2 |  | 4/T2 |  |  | Red | 2.5mm² H07Z-K | CON1/:4 | X-WLT | 3
[5 empty] | 13L- | [11 empty] | White | 2.5mm² H07Z-K | 13L- | X-WLT | 2
[5 empty] | 14L- | [11 empty] | White | 2.5mm² H07Z-K | 14L- | X-WLT | 4
B10E-PS-CUST-01 | HVEE Interlock | 24Vdc | 013 | 2 | DO2+ | X-DO 24 01 | X-CB 009 01 | 2a | Grey | 0.75mm² H05Z-K | 013/DO2+ | 4 | CON-6 | 7 |  | B10E-PS-CON-11 | Orange | 0.75mm² H05Z-K | 013/DO2+ | X-INTF07 | 39 | SEE | 0/2 | Tag change
[5 empty] | DO2- |  |  | 2b | White | 0.75mm² H05Z-K | 013/DO2- | 2 | (H4116) | 6 |  |  | Orange | 0.75mm² H05Z-K | 013/DO2- | X-INTF07 | 40 | DWG 73
B10E-PS-KEY-01:SOL | Beamline Enable Keyswitch Solenoid | 24Vdc | 013 | 3 | DO3+ | X-DO 24 01 | X-CB 009 01 | 3a | [6 empty] | ZCP | B10E-PS-KEY-01 | Grey | 0.75mm² H05Z-K | 013/DO3+ | X-ZCP | 1 | DO1 | 0
[5 empty] | DO3- |  |  | 3b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO3- | X-ZCP | 2
B10E-PS-KEY-02:SOL | Hutch Enable Keyswitch Solenoid | 24Vdc | 013 | 4 | DO4+ | X-DO 24 01 | X-CB 009 01 | 4a | [6 empty] | ZCP | B10E-PS-KEY-02 | Grey | 0.75mm² H05Z-K | 013/DO4+ | X-ZCP | 5 | DO1 | 0
[5 empty] | DO4- |  |  | 4b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO4- | X-ZCP | 6
B10E-PS-OR-01:LED | Door Open / Reset Pushbutton LED | 24Vdc | 013 | 5 | DO5+ | X-DO 24 01 | X-CB 009 01 | 5a | [6 empty] | ZCP | B10E-PS-OR-01 | Grey | 0.75mm² H05Z-K | 013/DO5+ | X-ZCP | 15 | DO1 | 0
[5 empty] | DO5- |  |  | 5b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO5- | X-ZCP | 16
B10E-PS-ASBF-01:LED | Area Search Button Final LED | 24Vdc | 013 | 6 | DO6+ | X-DO 24 01 | X-CB 009 01 | 6a | [6 empty] | ZCP | B10E-PS-ASBF-01 | Grey | 0.75mm² H05Z-K | 013/DO6+ | X-ZCP | 11 | DO1 | 0
[5 empty] | DO6- |  |  | 6b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO6- | X-ZCP | 12
B10E-PS-WLON-01:LED | White Lights Enable Switch LED | 24Vdc | 013 | 7 | DO7+ | X-DO 24 01 | X-CB 009 01 | 7a | [6 empty] | ZCP | B10E-PS-WLON-01 | Grey | 0.75mm² H05Z-K | 013/DO7+ | X-ZCP | 27 | DO1 | 0
[5 empty] | DO7- |  |  | 7b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO7- | X-ZCP | 28
B10E-PS-LCTx-01 | Light Curtain Test Function | 24Vdc | 013 | 8 | DO8+ | X-DO 24 01 | X-CB 009 01 | 8a | [6 empty] | EXTERNAL (VIA ZCP) | B10E-PS-LCTx-01 | Grey | 0.75mm² H05Z-K | 013/DO8+ | X-ZCP | 35 | DO1 | 0
[5 empty] | DO8- |  |  | 8b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO8- | X-ZCP | 36
B10E-PS-ANNOPN-01:A | Hutch Status Annunciator - OPEN A | 24Vdc | 013 | 9 | DO9+ | X-DO 24 01 | X-CB 009 01 | 9a | [6 empty] | EXTERNAL | B10E-PS-ANNUN-01 | Grey | 0.75mm² H05Z-K | 013/DO9+ | X-ANNUN | 1 | DO1 | 0
[5 empty] | DO9- |  |  | 9b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO9- | X-ANNUN | 2
B10E-PS-ANNRES-01:A | Hutch Status Annunciator - RESTRICTED A | 24Vdc | 013 | 10 | DO10+ | X-DO 24 01 | X-CB 009 01 | 10a | [6 empty] | EXTERNAL | B10E-PS-ANNUN-01 | Grey | 0.75mm² H05Z-K | 013/DO10+ | X-ANNUN | 5 | DO1 | 0
[5 empty] | DO10- |  |  | 10b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO10- | X-ANNUN | 6
B10E-PS-ANNSTB-01:A | Hutch Status Annunciator - STANDBY A | 24Vdc | 013 | 11 | DO11+ | X-DO 24 01 | X-CB 009 01 | 11a | [6 empty] | EXTERNAL | B10E-PS-ANNUN-01 | Grey | 0.75mm² H05Z-K | 013/DO11+ | X-ANNUN | 9 | DO1 | 0
[5 empty] | DO11- |  |  | 11b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO11- | X-ANNUN | 10
B10E-PS-ANNBON-01:A | Hutch Status Annunciator - BEAM ON A | 24Vdc | 013 | 12 | DO12+ | X-DO 24 01 | X-CB 009 01 | 12a | [6 empty] | EXTERNAL | B10E-PS-ANNUN-01 | Grey | 0.75mm² H05Z-K | 013/DO12+ | X-ANNUN | 13 | DO1 | 0
[5 empty] | DO12- |  |  | 12b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO12- | X-ANNUN | 14
B10E-PS-SP01-01 | Beacon/Sounder 01 Message 1 (LSB) | 24Vdc | 013 | 13 | DO13+ | X-DO 24 01 | X-CB 009 01 | 13a | [6 empty] | HUTCH | B10E-PS-SP-01 | Grey | 0.75mm² H05Z-K | 013/DO13+ | X-SP01 | 1 | DO1 | 0
[5 empty] | DO13- |  |  | 13b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO13- | X-SP01 | 2
B10E-PS-SP02-01 | Beacon/Sounder 01 Message 2 (MSB) | 24Vdc | 013 | 14 | DO14+ | X-DO 24 01 | X-CB 009 01 | 14a | [6 empty] | HUTCH | B10E-PS-SP-01 | Grey | 0.75mm² H05Z-K | 013/DO14+ | X-SP01 | 3 | DO1 | 0
[5 empty] | DO14- |  |  | 14b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO14- | X-SP01 | 4
B10E-PS-SP03-01 | Beacon/Sounder 01 Strobe | 24Vdc | 013 | 15 | DO15+ | X-DO 24 01 | X-CB 009 01 | 15a | [6 empty] | HUTCH | B10E-PS-SP-01 | Grey | 0.75mm² H05Z-K | 013/DO15+ | X-SP01 | 5 | DO1 | 0
[5 empty] | DO15- |  |  | 15b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO15- | X-SP01 | 6
B10E-PS-SOVLN2-01 | Liquid Nitrogen Shuttoff Valve | 24Vdc | 013 | 16 | DO16+ | X-DO 24 01 | X-CB 009 01 | 16a | [6 empty] | EXTERNAL | B10E-PS-SOVLN2-01 | Grey | 0.75mm² H05Z-K | 013/DO16+ | X-SOVLN2 | 1 | DO1 | 0
[5 empty] | DO16- |  |  | 16b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO16- | X-SOVLN2 | 2
B10E-PS-SP01-04 | O2/SF6 Healthy Beacon 01 (Green LED) | 24Vdc | 013 | 17 | DO17+ | X-DO 24 01 | X-CB 009 01 | 17a | [6 empty] | HUTCH | B10E-PS-SP-04 | Grey | 0.75mm² H05Z-K | 013/DO17+ | X-SP | 1 | DO1 | 0
[5 empty] | DO17- |  |  | 17b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO17- | X-SP | 2
B10E-PS-SP02-04 | O2/SF6 Alarm Beacon 01 (Red LED) | 24Vdc | 013 | 18 | DO18+ | X-DO 24 01 | X-CB 009 01 | 18a | [6 empty] | HUTCH | B10E-PS-SP-04 | Grey | 0.75mm² H05Z-K | 013/DO18+ | X-SP | 3 | DO1 | 0
[5 empty] | DO18- |  |  | 18b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO18- | X-SP | 4
B10E-PS-CON-06:EN | Power Contactor 06 (3 Phase RF Power) | 24Vdc | 013 | 19 | DO19+ | X-DO 24 01 | X-CB 009 01 | 19a | [6 empty] | ELECTRON SOURCE | B10E-PS-CON-06 | Grey | 0.75mm² H05Z-K | 013/DO19+ | X-INTF07 | 43 | DO1 | 0/2
[5 empty] | DO19- |  |  | 19b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO19- | X-INTF07 | 44
B10E-PS-CON-07:EN | Power Contactor 07 (3 Phase RF Power) | 24Vdc | 013 | 20 | DO20+ | X-DO 24 01 | X-CB 009 01 | 20a | [6 empty] | ELECTRON SOURCE | B10E-PS-CON-07 | Grey | 0.75mm² H05Z-K | 013/DO20+ | X-INTF07 | 47 | DO1 | 0/2
[5 empty] | DO20- |  |  | 20b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO20- | X-INTF07 | 48
B10E-PS-CON-08:EN | Power Contactor 08 (3 Phase RF Power) | 24Vdc | 013 | 21 | DO21+ | X-DO 24 01 | X-CB 009 01 | 21a | [6 empty] | ELECTRON SOURCE | B10E-PS-CON-08 | Grey | 0.75mm² H05Z-K | 013/DO21+ | X-INTF07 | 51 | DO1 | 0/2
[5 empty] | DO21- |  |  | 21b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO21- | X-INTF07 | 52
B10E-PS-CON-09:EN | Power Contactor 09 (1 Phase RF Drive) | 24Vdc | 013 | 22 | DO22+ | X-DO 24 01 | X-CB 009 01 | 22a | [6 empty] | ELECTRON SOURCE | B10E-PS-CON-09 | Grey | 0.75mm² H05Z-K | 013/DO22+ | X-INTF07 | 55 | DO1 | 0/2
[5 empty] | DO22- |  |  | 22b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO22- | X-INTF07 | 56
B10E-PS-CON-10:EN | Power Contactor 10 (1 Phase RF Drive) | 24Vdc | 013 | 23 | DO23+ | X-DO 24 01 | X-CB 009 01 | 23a | [6 empty] | ELECTRON SOURCE | B10E-PS-CON-10 | Grey | 0.75mm² H05Z-K | 013/DO23+ | X-INTF07 | 59 | DO1 | 0/2
[5 empty] | DO23- |  |  | 23b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO23- | X-INTF07 | 60
SPDO-013/24 | Wired Spare Output | 24Vdc | 013 | 24 | DO24+ | X-DO 24 01 | X-CB 009 01 | 24a | [8 empty] | Grey | 0.75mm² H05Z-K | 013/DO24+ | X-SPDO | 11 | DO1 | 0
[5 empty] | DO24- |  |  | 24b | [8 empty] | White | 0.75mm² H05Z-K | 013/DO24- | X-SPDO | 12

## 014_DO
TAG | DESCRIPTION | SIGNAL TYPE | CHASSIS &SLOT No | Channel. No. | Signal | MODULE | CONNECTION BOARD | CB TERM. | DEVICE LOCATION | DEVICE TAG | WIRE COLOUR | WIRE TYPE | WIRE NUMBER | TERMINAL BLOCK | TERM. No. | Loop Type | REV.
B10E-PS-ASB-01:LED | Area Search Pushbutton LED 01 | 24Vdc | 014 | 1 | DO1+ | X-DO 24 01 | X-CB 009 01 | 1a | HUTCH | B10E-PS-ASB-01 | Grey | 0.75mm² H05Z-K | 014/DO1+ | X-ASB | 3 | DO1 | 0
[5 empty] | DO1- |  |  | 1b |  |  | White | 0.75mm² H05Z-K | 014/DO1- | X-ASB | 4
B10E-PS-ASB-02:LED | Area Search Pushbutton LED 02 | 24Vdc | 014 | 2 | DO2+ | X-DO 24 01 | X-CB 009 01 | 2a | HUTCH | B10E-PS-ASB-02 | Grey | 0.75mm² H05Z-K | 014/DO2+ | X-ASB | 7 | DO1 | 0
[5 empty] | DO2- |  |  | 2b |  |  | White | 0.75mm² H05Z-K | 014/DO2- | X-ASB | 8
B10E-PS-ASB-03:LED | Area Search Pushbutton LED 03 | 24Vdc | 014 | 3 | DO3+ | X-DO 24 01 | X-CB 009 01 | 3a | HUTCH | B10E-PS-ASB-03 | Grey | 0.75mm² H05Z-K | 014/DO3+ | X-ASB | 11 | DO1 | 0
[5 empty] | DO3- |  |  | 3b |  |  | White | 0.75mm² H05Z-K | 014/DO3- | X-ASB | 12
B10E-PS-ASB-04:LED | Area Search Pushbutton LED 04 | 24Vdc | 014 | 4 | DO4+ | X-DO 24 01 | X-CB 009 01 | 4a | HUTCH | B10E-PS-ASB-04 | Grey | 0.75mm² H05Z-K | 014/DO4+ | X-ASB | 15 | DO1 | 0
[5 empty] | DO4- |  |  | 4b |  |  | White | 0.75mm² H05Z-K | 014/DO4- | X-ASB | 16
B10E-PS-SP01-02 | Beacon/Sounder 02 Message 1 (LSB) | 24Vdc | 014 | 5 | DO5+ | X-DO 24 01 | X-CB 009 01 | 5a | HUTCH | B10E-PS-SP-02 | Grey | 0.75mm² H05Z-K | 014/DO5+ | X-SP02 | 1 | DO1 | 0
[5 empty] | DO5- |  |  | 5b |  |  | White | 0.75mm² H05Z-K | 014/DO5- | X-SP02 | 2
B10E-PS-SP02-02 | Beacon/Sounder 02 Message 2 (MSB) | 24Vdc | 014 | 6 | DO6+ | X-DO 24 01 | X-CB 009 01 | 6a | HUTCH | B10E-PS-SP-02 | Grey | 0.75mm² H05Z-K | 014/DO6+ | X-SP02 | 3 | DO1 | 0
[5 empty] | DO6- |  |  | 6b |  |  | White | 0.75mm² H05Z-K | 014/DO6- | X-SP02 | 4
B10E-PS-SP03-02 | Beacon/Sounder 02 Strobe | 24Vdc | 014 | 7 | DO7+ | X-DO 24 01 | X-CB 009 01 | 7a | HUTCH | B10E-PS-SP-02 | Grey | 0.75mm² H05Z-K | 014/DO7+ | X-SP02 | 5 | DO1 | 0
[5 empty] | DO7- |  |  | 7b |  |  | White | 0.75mm² H05Z-K | 014/DO7- | X-SP02 | 6
SPDO-014/8 | Wired Spare Output | 24Vdc | 014 | 8 | DO8+ | X-DO 24 01 | X-CB 009 01 | 8a |  |  | Grey | 0.75mm² H05Z-K | 014/DO8+ | X-SPDO | 13 | DO1 | 0
[5 empty] | DO8- |  |  | 8b |  |  | White | 0.75mm² H05Z-K | 014/DO8- | X-SPDO | 14
B10E-PS-ANNOPN-01:B | Hutch Status Annunciator - OPEN B | 24Vdc | 014 | 9 | DO9+ | X-DO 24 01 | X-CB 009 01 | 9a | EXTERNAL | B10E-PS-ANNUN-01 | Grey | 0.75mm² H05Z-K | 014/DO9+ | X-ANNUN | 3 | DO1 | 0
[5 empty] | DO9- |  |  | 9b |  |  | White | 0.75mm² H05Z-K | 014/DO9- | X-ANNUN | 4
B10E-PS-ANNRES-01:B | Hutch Status Annunciator - RESTRICTED B | 24Vdc | 014 | 10 | DO10+ | X-DO 24 01 | X-CB 009 01 | 10a | EXTERNAL | B10E-PS-ANNUN-01 | Grey | 0.75mm² H05Z-K | 014/DO10+ | X-ANNUN | 7 | DO1 | 0
[5 empty] | DO10- |  |  | 10b |  |  | White | 0.75mm² H05Z-K | 014/DO10- | X-ANNUN | 8
B10E-PS-ANNSTB-01:B | Hutch Status Annunciator - STANDBY B | 24Vdc | 014 | 11 | DO11+ | X-DO 24 01 | X-CB 009 01 | 11a | EXTERNAL | B10E-PS-ANNUN-01 | Grey | 0.75mm² H05Z-K | 014/DO11+ | X-ANNUN | 11 | DO1 | 0
[5 empty] | DO11- |  |  | 11b |  |  | White | 0.75mm² H05Z-K | 014/DO11- | X-ANNUN | 12
B10E-PS-ANNBON-01:B | Hutch Status Annunciator - BEAM ON B | 24Vdc | 014 | 12 | DO12+ | X-DO 24 01 | X-CB 009 01 | 12a | EXTERNAL | B10E-PS-ANNUN-01 | Grey | 0.75mm² H05Z-K | 014/DO12+ | X-ANNUN | 15 | DO1 | 0
[5 empty] | DO12- |  |  | 12b |  |  | White | 0.75mm² H05Z-K | 014/DO12- | X-ANNUN | 16
B10E-PS-SP01-05 | O2/SF6 Healthy Beacon 02 (GREEN LED) | 24Vdc | 014 | 13 | DO13+ | X-DO 24 01 | X-CB 009 01 | 13a | HUTCH | B10E-PS-SP-05 | Grey | 0.75mm² H05Z-K | 014/DO13+ | X-SP | 5 | DO1 | 0
[5 empty] | DO13- |  |  | 13b |  |  | White | 0.75mm² H05Z-K | 014/DO13- | X-SP | 6
B10E-PS-SP02-05 | O2/SF6 Alarm Beacon 02 (RED LED) | 24Vdc | 014 | 14 | DO14+ | X-DO 24 01 | X-CB 009 01 | 14a | HUTCH | B10E-PS-SP-05 | Grey | 0.75mm² H05Z-K | 014/DO14+ | X-SP | 7 | DO1 | 0
[5 empty] | DO14- |  |  | 14b |  |  | White | 0.75mm² H05Z-K | 014/DO14- | X-SP | 8
B10E-PS-BLUEL-01:A | Blue Light 01 -A | 24Vdc | 014 | 15 | DO15+ | X-DO 24 01 | X-CB 009 01 | 15a | HUTCH | B10E-PS-BLUEL-01 | Grey | 0.75mm² H05Z-K | 014/DO15+ | X-BLUEL | 1 | DO1 | 0
[5 empty] | DO15- |  |  | 15b |  |  | White | 0.75mm² H05Z-K | 014/DO15- | X-BLUEL | 2
B10E-PS-BLUEL-02:A | Blue Light 02 -A | 24Vdc | 014 | 16 | DO16+ | X-DO 24 01 | X-CB 009 01 | 16a | HUTCH | B10E-PS-BLUEL-02 | Grey | 0.75mm² H05Z-K | 014/DO16+ | X-BLUEL | 5 | DO1 | 0
[5 empty] | DO16- |  |  | 16b |  |  | White | 0.75mm² H05Z-K | 014/DO16- | X-BLUEL | 6
B10E-PS-BLUEL-03:A | Blue Light 03 -A | 24Vdc | 014 | 17 | DO17+ | X-DO 24 01 | X-CB 009 01 | 17a | HUTCH | B10E-PS-BLUEL-03 | Grey | 0.75mm² H05Z-K | 014/DO17+ | X-BLUEL | 9 | DO1 | 0
[5 empty] | DO17- |  |  | 17b |  |  | White | 0.75mm² H05Z-K | 014/DO17- | X-BLUEL | 10
B10E-PS-BLUEL-04:A | Blue Light 04 -A | 24Vdc | 014 | 18 | DO18+ | X-DO 24 01 | X-CB 009 01 | 18a | HUTCH | B10E-PS-BLUEL-04 | Grey | 0.75mm² H05Z-K | 014/DO18+ | X-BLUEL | 13 | DO1 | 0
[5 empty] | DO18- |  |  | 18b |  |  | White | 0.75mm² H05Z-K | 014/DO18- | X-BLUEL | 14
B10E-PS-BLUEL-05:A | Blue Light 05 -A | 24Vdc | 014 | 19 | DO19+ | X-DO 24 01 | X-CB 009 01 | 19a | HUTCH | B10E-PS-BLUEL-05 | Grey | 0.75mm² H05Z-K | 014/DO19+ | X-BLUEL | 17 | DO1 | 0
[5 empty] | DO19- |  |  | 19b |  |  | White | 0.75mm² H05Z-K | 014/DO19- | X-BLUEL | 18
B10E-PS-BLUEL-06:A | Blue Light 06 -A | 24Vdc | 014 | 20 | DO20+ | X-DO 24 01 | X-CB 009 01 | 20a | HUTCH | B10E-PS-BLUEL-06 | Grey | 0.75mm² H05Z-K | 014/DO20+ | X-BLUEL | 21 | DO1 | 0
[5 empty] | DO20- |  |  | 20b |  |  | White | 0.75mm² H05Z-K | 014/DO20- | X-BLUEL | 22
SPDO-014/21 | Wired Spare Output | 24Vdc | 014 | 21 | DO21+ | X-DO 24 01 | X-CB 009 01 | 21a |  |  | Grey | 0.75mm² H05Z-K | 014/DO21+ | X-SPDO | 15 | DO1 | 0
[5 empty] | DO21- |  |  | 21b |  |  | White | 0.75mm² H05Z-K | 014/DO21- | X-SPDO | 16
SPDO-014/22 | Wired Spare Output | 24Vdc | 014 | 22 | DO22+ | X-DO 24 01 | X-CB 009 01 | 22a |  |  | Grey | 0.75mm² H05Z-K | 014/DO22+ | X-SPDO | 17 | DO1 | 0
[5 empty] | DO22- |  |  | 22b |  |  | White | 0.75mm² H05Z-K | 014/DO22- | X-SPDO | 18
SPDO-014/23 | Wired Spare Output | 24Vdc | 014 | 23 | DO23+ | X-DO 24 01 | X-CB 009 01 | 23a |  |  | Grey | 0.75mm² H05Z-K | 014/DO23+ | X-SPDO | 19 | DO1 | 0
[5 empty] | DO23- |  |  | 23b |  |  | White | 0.75mm² H05Z-K | 014/DO23- | X-SPDO | 20
SPDO-013/23 | Wired Spare Output | 24Vdc | 014 | 24 | DO24+ | X-DO 24 01 | X-CB 009 01 | 24a |  |  | Grey | 0.75mm² H05Z-K | 014/DO24+ | X-SPDO | 21 | DO1 | 0
[5 empty] | DO24- |  |  | 24b |  |  | White | 0.75mm² H05Z-K | 014/DO24- | X-SPDO | 22

## 015_DO
TAG | DESCRIPTION | SIGNAL TYPE | CHASSIS &SLOT No | Channel. No. | Signal | MODULE | CONNECTION BOARD | CB TERM. | DEVICE LOCATION | DEVICE TAG | WIRE COLOUR | WIRE TYPE | WIRE NUMBER | TERMINAL BLOCK | TERM. No. | Loop Type | REV.
B10E-PS-SP01-03 | Beacon/Sounder 03 Message 1 | 24Vdc | 015 | 1 | DO1+ | X-DO 24 01 | X-CB 009 01 | 1a | HUTCH | B10E-PS-SP-03 | Grey | 0.75mm² H05Z-K | 015/DO1+ | X-SP03 | 1 | DO1 | 0
[5 empty] | DO1- |  |  | 1b |  |  | White | 0.75mm² H05Z-K | 015/DO1- | X-SP03 | 2
B10E-PS-SP02-03 | Beacon/Sounder 03 Message 2 | 24Vdc | 015 | 2 | DO2+ | X-DO 24 01 | X-CB 009 01 | 2a | HUTCH | B10E-PS-SP-03 | Grey | 0.75mm² H05Z-K | 015/DO2+ | X-SP03 | 3 | DO1 | 0
[5 empty] | DO2- |  |  | 2b |  |  | White | 0.75mm² H05Z-K | 015/DO2- | X-SP03 | 4
B10E-PS-SP03-03 | Beacon/Sounder 03 Strobe | 24Vdc | 015 | 3 | DO3+ | X-DO 24 01 | X-CB 009 01 | 3a | HUTCH | B10E-PS-SP-03 | Grey | 0.75mm² H05Z-K | 015/DO3+ | X-SP03 | 5 | DO1 | 0
[5 empty] | DO3- |  |  | 3b |  |  | White | 0.75mm² H05Z-K | 015/DO3- | X-SP03 | 6
B10E-PS-BOBI-01:A | Beam Off Button Indicator 01 -A | 24Vdc | 015 | 4 | DO4+ | X-DO 24 01 | X-CB 009 01 | 4a | HUTCH | B10E-PS-BOBI-01 | Grey | 0.75mm² H05Z-K | 015/DO4+ | X-BOBI | 1 | DO1 | 0
[5 empty] | DO4- |  |  | 4b |  |  | White | 0.75mm² H05Z-K | 015/DO4- | X-BOBI | 2
B10E-PS-BOBI-02:A | Beam Off Button Indicator 02 -A | 24Vdc | 015 | 5 | DO5+ | X-DO 24 01 | X-CB 009 01 | 5a | HUTCH | B10E-PS-BOBI-02 | Grey | 0.75mm² H05Z-K | 015/DO5+ | X-BOBI | 5 | DO1 | 0
[5 empty] | DO5- |  |  | 5b |  |  | White | 0.75mm² H05Z-K | 015/DO5- | X-BOBI | 6
B10E-PS-BOBI-03:A | Beam Off Button Indicator 03 -A | 24Vdc | 015 | 6 | DO6+ | X-DO 24 01 | X-CB 009 01 | 6a | HUTCH | B10E-PS-BOBI-03 | Grey | 0.75mm² H05Z-K | 015/DO6+ | X-BOBI | 9 | DO1 | 0
[5 empty] | DO6- |  |  | 6b |  |  | White | 0.75mm² H05Z-K | 015/DO6- | X-BOBI | 10
B10E-PS-BOBI-04:A | Beam Off Button Indicator 04 -A | 24Vdc | 015 | 7 | DO7+ | X-DO 24 01 | X-CB 009 01 | 7a | HUTCH | B10E-PS-BOBI-04 | Grey | 0.75mm² H05Z-K | 015/DO7+ | X-BOBI | 13 | DO1 | 0
[5 empty] | DO7- |  |  | 7b |  |  | White | 0.75mm² H05Z-K | 015/DO7- | X-BOBI | 14
B10E-PS-BOBI-05:A | Beam Off Button Indicator 05 -A | 24Vdc | 015 | 8 | DO8+ | X-DO 24 01 | X-CB 009 01 | 8a | HUTCH | B10E-PS-BOBI-05 | Grey | 0.75mm² H05Z-K | 015/DO8+ | X-BOBI | 17 | DO1 | 0
[5 empty] | DO8- |  |  | 8b |  |  | White | 0.75mm² H05Z-K | 015/DO8- | X-BOBI | 18
B10E-PS-BONI-01:A | Beam On Indicator 01 -A | 24Vdc | 015 | 9 | DO9+ | X-DO 24 01 | X-CB 009 01 | 9a | HUTCH | B10E-PS-BONI-01 | Grey | 0.75mm² H05Z-K | 015/DO9+ | X-BOBI | 21 | DO1 | 0
[5 empty] | DO9- |  |  | 9b |  |  | White | 0.75mm² H05Z-K | 015/DO9- | X-BOBI | 22
B10E-PS-SP01-06 | O2/SF6 Healthy Beacon 03 (GREEN LED) | 24Vdc | 015 | 10 | DO10+ | X-DO 24 01 | X-CB 009 01 | 10a | HUTCH | B10E-PS-SP-06 | Grey | 0.75mm² H05Z-K | 015/DO10+ | X-SP | 9 | DO1 | 0
[5 empty] | DO10- |  |  | 10b |  |  | White | 0.75mm² H05Z-K | 015/DO10- | X-SP | 10
B10E-PS-SP02-06 | O2/SF6 Alarm Beacon 03 (RED LED) | 24Vdc | 015 | 11 | DO11+ | X-DO 24 01 | X-CB 009 01 | 11a | HUTCH | B10E-PS-SP-06 | Grey | 0.75mm² H05Z-K | 015/DO11+ | X-SP | 11 | DO1 | 0
[5 empty] | DO11- |  |  | 11b |  |  | White | 0.75mm² H05Z-K | 015/DO11- | X-SP | 12
B10E-PS-SP01-07 | O2/SF6 Healthy Beacon 04 (GREEN LED) | 24Vdc | 015 | 12 | DO12+ | X-DO 24 01 | X-CB 009 01 | 12a | EXTERNAL | B10E-PS-SP-07 | Grey | 0.75mm² H05Z-K | 015/DO12+ | X-SP | 13 | DO1 | 0
[5 empty] | DO12- |  |  | 12b |  |  | White | 0.75mm² H05Z-K | 015/DO12- | X-SP | 14
B10E-PS-SP02-07 | O2/SF6 Alarm Beacon 04 (RED LED) | 24Vdc | 015 | 13 | DO13+ | X-DO 24 01 | X-CB 009 01 | 13a | EXTERNAL | B10E-PS-SP-07 | Grey | 0.75mm² H05Z-K | 015/DO13+ | X-SP | 15 | DO1 | 0
[5 empty] | DO13- |  |  | 13b |  |  | White | 0.75mm² H05Z-K | 015/DO13- | X-SP | 16
SPDO-015/14 | Wired Spare Output | 24Vdc | 015 | 14 | DO14+ | X-DO 24 01 | X-CB 009 01 | 14a |  |  | Grey | 0.75mm² H05Z-K | 015/DO14+ | X-SPDO | 23 | DO1 | 0
[5 empty] | DO14- |  |  | 14b |  |  | White | 0.75mm² H05Z-K | 015/DO14- | X-SPDO | 24
B10E-PS-BLUEL-01:B | Blue Light 01 -B | 24Vdc | 015 | 15 | DO15+ | X-DO 24 01 | X-CB 009 01 | 15a | HUTCH | B10E-PS-BLUEL-01 | Grey | 0.75mm² H05Z-K | 015/DO15+ | X-BLUEL | 3 | DO1 | 0
[5 empty] | DO15- |  |  | 15b |  |  | White | 0.75mm² H05Z-K | 015/DO15- | X-BLUEL | 4
B10E-PS-BLUEL-02:B | Blue Light 02 -B | 24Vdc | 015 | 16 | DO16+ | X-DO 24 01 | X-CB 009 01 | 16a | HUTCH | B10E-PS-BLUEL-02 | Grey | 0.75mm² H05Z-K | 015/DO16+ | X-BLUEL | 7 | DO1 | 0
[5 empty] | DO16- |  |  | 16b |  |  | White | 0.75mm² H05Z-K | 015/DO16- | X-BLUEL | 8
B10E-PS-BLUEL-03:B | Blue Light 03 -B | 24Vdc | 015 | 17 | DO17+ | X-DO 24 01 | X-CB 009 01 | 17a | HUTCH | B10E-PS-BLUEL-03 | Grey | 0.75mm² H05Z-K | 015/DO17+ | X-BLUEL | 11 | DO1 | 0
[5 empty] | DO17- |  |  | 17b |  |  | White | 0.75mm² H05Z-K | 015/DO17- | X-BLUEL | 12
B10E-PS-BLUEL-04:B | Blue Light 04 -B | 24Vdc | 015 | 18 | DO18+ | X-DO 24 01 | X-CB 009 01 | 18a | HUTCH | B10E-PS-BLUEL-04 | Grey | 0.75mm² H05Z-K | 015/DO18+ | X-BLUEL | 15 | DO1 | 0
[5 empty] | DO18- |  |  | 18b |  |  | White | 0.75mm² H05Z-K | 015/DO18- | X-BLUEL | 16
B10E-PS-BLUEL-05:B | Blue Light 05 -B | 24Vdc | 015 | 19 | DO19+ | X-DO 24 01 | X-CB 009 01 | 19a | HUTCH | B10E-PS-BLUEL-05 | Grey | 0.75mm² H05Z-K | 015/DO19+ | X-BLUEL | 19 | DO1 | 0
[5 empty] | DO19- |  |  | 19b |  |  | White | 0.75mm² H05Z-K | 015/DO19- | X-BLUEL | 20
B10E-PS-BLUEL-06:B | Blue Light 06 -B | 24Vdc | 015 | 20 | DO20+ | X-DO 24 01 | X-CB 009 01 | 20a | HUTCH | B10E-PS-BLUEL-06 | Grey | 0.75mm² H05Z-K | 015/DO20+ | X-BLUEL | 23 | DO1 | 0
[5 empty] | DO20- |  |  | 20b |  |  | White | 0.75mm² H05Z-K | 015/DO20- | X-BLUEL | 24
SPDO-015/21 | Wired Spare Output | 24Vdc | 015 | 21 | DO21+ | X-DO 24 01 | X-CB 009 01 | 21a |  |  | Grey | 0.75mm² H05Z-K | 015/DO21+ | X-SPDO | 25 | DO1 | 0
[5 empty] | DO21- |  |  | 21b |  |  | White | 0.75mm² H05Z-K | 015/DO21- | X-SPDO | 26
SPDO-015/22 | Wired Spare Output | 24Vdc | 015 | 22 | DO22+ | X-DO 24 01 | X-CB 009 01 | 22a |  |  | Grey | 0.75mm² H05Z-K | 015/DO22+ | X-SPDO | 27 | DO1 | 0
[5 empty] | DO22- |  |  | 22b |  |  | White | 0.75mm² H05Z-K | 015/DO22- | X-SPDO | 28
SPDO-015/23 | Wired Spare Output | 24Vdc | 015 | 23 | DO23+ | X-DO 24 01 | X-CB 009 01 | 23a |  |  | Grey | 0.75mm² H05Z-K | 015/DO23+ | X-SPDO | 29 | DO1 | 0
[5 empty] | DO23- |  |  | 23b |  |  | White | 0.75mm² H05Z-K | 015/DO23- | X-SPDO | 30
SPDO-013/23 | Wired Spare Output | 24Vdc | 015 | 24 | DO24+ | X-DO 24 01 | X-CB 009 01 | 24a |  |  | Grey | 0.75mm² H05Z-K | 015/DO24+ | X-SPDO | 31 | DO1 | 0
[5 empty] | DO24- |  |  | 24b |  |  | White | 0.75mm² H05Z-K | 015/DO24- | X-SPDO | 32

## 016_DO
TAG | DESCRIPTION | SIGNAL TYPE | CHASSIS &SLOT No | Channel. No. | Signal | MODULE | CONNECTION BOARD | CB TERM. | DEVICE LOCATION | DEVICE TAG | WIRE COLOUR | WIRE TYPE | WIRE NUMBER | TERMINAL BLOCK | TERM. No. | Loop Type | REV.
SPDO-016/1 | Wired Spare Output | 24Vdc | 016 | 1 | DO1+ | X-DO 24 01 | X-CB 009 01 | 1a |  |  | Grey | 0.75mm² H05Z-K | 016/DO1+ | X-SPDO | 33 | DO1 | 0
[5 empty] | DO1- |  |  | 1b |  |  | White | 0.75mm² H05Z-K | 016/DO1- | X-SPDO | 34
SPDO-016/2 | Wired Spare Output | 24Vdc | 016 | 2 | DO2+ | X-DO 24 01 | X-CB 009 01 | 2a |  |  | Grey | 0.75mm² H05Z-K | 016/DO2+ | X-SPDO | 35 | DO1 | 0
[5 empty] | DO2- |  |  | 2b |  |  | White | 0.75mm² H05Z-K | 016/DO2- | X-SPDO | 36
SPDO-016/3 | Wired Spare Output | 24Vdc | 016 | 3 | DO3+ | X-DO 24 01 | X-CB 009 01 | 3a |  |  | Grey | 0.75mm² H05Z-K | 016/DO3+ | X-SPDO | 37 | DO1 | 0
[5 empty] | DO3- |  |  | 3b |  |  | White | 0.75mm² H05Z-K | 016/DO3- | X-SPDO | 38
B10E-PS-BOBI-01:B | Beam Off Button Indicator 01 -B | 24Vdc | 016 | 4 | DO4+ | X-DO 24 01 | X-CB 009 01 | 4a | HUTCH | B10E-PS-BOBI-01 | Grey | 0.75mm² H05Z-K | 016/DO4+ | X-BOBI | 3 | DO1 | 0
[5 empty] | DO4- |  |  | 4b |  |  | White | 0.75mm² H05Z-K | 016/DO4- | X-BOBI | 4
B10E-PS-BOBI-02:B | Beam Off Button Indicator 02 -B | 24Vdc | 016 | 5 | DO5+ | X-DO 24 01 | X-CB 009 01 | 5a | HUTCH | B10E-PS-BOBI-02 | Grey | 0.75mm² H05Z-K | 016/DO5+ | X-BOBI | 7 | DO1 | 0
[5 empty] | DO5- |  |  | 5b |  |  | White | 0.75mm² H05Z-K | 016/DO5- | X-BOBI | 8
B10E-PS-BOBI-03:B | Beam Off Button Indicator 03 -B | 24Vdc | 016 | 6 | DO6+ | X-DO 24 01 | X-CB 009 01 | 6a | HUTCH | B10E-PS-BOBI-03 | Grey | 0.75mm² H05Z-K | 016/DO6+ | X-BOBI | 11 | DO1 | 0
[5 empty] | DO6- |  |  | 6b |  |  | White | 0.75mm² H05Z-K | 016/DO6- | X-BOBI | 12
B10E-PS-BOBI-04:B | Beam Off Button Indicator 04 -B | 24Vdc | 016 | 7 | DO7+ | X-DO 24 01 | X-CB 009 01 | 7a | HUTCH | B10E-PS-BOBI-04 | Grey | 0.75mm² H05Z-K | 016/DO7+ | X-BOBI | 15 | DO1 | 0
[5 empty] | DO7- |  |  | 7b |  |  | White | 0.75mm² H05Z-K | 016/DO7- | X-BOBI | 16
B10E-PS-BOBI-05:B | Beam Off Button Indicator 05 -B | 24Vdc | 016 | 8 | DO8+ | X-DO 24 01 | X-CB 009 01 | 8a | HUTCH | B10E-PS-BOBI-05 | Grey | 0.75mm² H05Z-K | 016/DO8+ | X-BOBI | 19 | DO1 | 0
[5 empty] | DO8- |  |  | 8b |  |  | White | 0.75mm² H05Z-K | 016/DO8- | X-BOBI | 20
B10E-PS-BONI-01:B | Beam On Indicator 01 -B | 24Vdc | 016 | 9 | DO9+ | X-DO 24 01 | X-CB 009 01 | 9a | HUTCH | B10E-PS-BONI-01 | Grey | 0.75mm² H05Z-K | 016/DO9+ | X-BOBI | 23 | DO1 | 0
[5 empty] | DO9- |  |  | 9b |  |  | White | 0.75mm² H05Z-K | 016/DO9- | X-BOBI | 24
B10E-PS-CON-01:EN | Power Contactor 01 | 24Vdc | 016 | 10 | DO10+ | X-DO 24 01 | X-CB 009 01 | 10a | ELECTRON SOURCE | B10E-PS-CON-01 | Grey | 0.75mm² H05Z-K | 016/DO10+ | X-INTF07 | 1 | DO1 | 0
[5 empty] | DO10- |  |  | 10b |  |  | White | 0.75mm² H05Z-K | 016/DO10- | X-INTF07 | 2
B10E-PS-CON-02:EN | Power Contactor 02 | 24Vdc | 016 | 11 | DO11+ | X-DO 24 01 | X-CB 009 01 | 11a | ELECTRON SOURCE | B10E-PS-CON-02 | Grey | 0.75mm² H05Z-K | 016/DO11+ | X-INTF07 | 5 | DO1 | 0
[5 empty] | DO11- |  |  | 11b |  |  | White | 0.75mm² H05Z-K | 016/DO11- | X-INTF07 | 6
B10E-PS-CON-03:EN | Power Contactor 03 | 24Vdc | 016 | 12 | DO12+ | X-DO 24 01 | X-CB 009 01 | 12a | ELECTRON SOURCE | B10E-PS-CON-03 | Grey | 0.75mm² H05Z-K | 016/DO12+ | X-INTF07 | 9 | DO1 | 0
[5 empty] | DO12- |  |  | 12b |  |  | White | 0.75mm² H05Z-K | 016/DO12- | X-INTF07 | 10
B10E-PS-CON-04:EN | Power Contactor 04 | 24Vdc | 016 | 13 | DO13+ | X-DO 24 01 | X-CB 009 01 | 13a | ELECTRON SOURCE | B10E-PS-CON-04 | Grey | 0.75mm² H05Z-K | 016/DO13+ | X-INTF07 | 13 | DO1 | 0
[5 empty] | DO13- |  |  | 13b |  |  | White | 0.75mm² H05Z-K | 016/DO13- | X-INTF07 | 14
B10E-PS-CON-05:EN | Power Contactor 05 | 24Vdc | 016 | 14 | DO14+ | X-DO 24 01 | X-CB 009 01 | 14a | ELECTRON SOURCE | B10E-PS-CON-05 | Grey | 0.75mm² H05Z-K | 016/DO14+ | X-INTF07 | 17 | DO1 | 0
[5 empty] | DO14- |  |  | 14b |  |  | White | 0.75mm² H05Z-K | 016/DO14- | X-INTF07 | 18
B10E-PS-SOL-01 | Lock General Access Door Switch 1 | 24Vdc | 016 | 15 | DO15+ | X-DO 24 01 | X-CB 009 01 | 15a | EXTERNAL | B10E-PS-DS-01 | Grey | 0.75mm² H05Z-K | 016/DO15+ | X-DS01 | 7 | DO1 | 0
[5 empty] | DO15- |  |  | 15b |  |  | White | 0.75mm² H05Z-K | 016/DO15- | X-DS01 | 8
B10E-PS-SOL-02 | Lock General Access Door Switch 2 | 24Vdc | 016 | 16 | DO16+ | X-DO 24 01 | X-CB 009 01 | 16a | EXTERNAL | B10E-PS-DS-02 | Grey | 0.75mm² H05Z-K | 016/DO16+ | X-DS02 | 7 | DO1 | 0
[5 empty] | DO16- |  |  | 16b |  |  | White | 0.75mm² H05Z-K | 016/DO16- | X-DS02 | 8
B10E-PS-SOL-03 | Lock General Access Gate Switch 1 | 24Vdc | 016 | 17 | DO17+ | X-DO 24 01 | X-CB 009 01 | 17a | EXTERNAL | B10E-PS-DS-04 | Grey | 0.75mm² H05Z-K | 016/DO17+ | X-DS04 | 7 | DO1 | 0
[5 empty] | DO17- |  |  | 17b |  |  | White | 0.75mm² H05Z-K | 016/DO17- | X-DS04 | 8
B10E-PS-SOL-04 | Lock General Access Gate Switch 2 | 24Vdc | 016 | 18 | DO18+ | X-DO 24 01 | X-CB 009 01 | 18a | EXTERNAL | B10E-PS-DS-05 | Grey | 0.75mm² H05Z-K | 016/DO18+ | X-DS05 | 7 | DO1 | 0
[5 empty] | DO18- |  |  | 18b |  |  | White | 0.75mm² H05Z-K | 016/DO18- | X-DS05 | 8
B10E-PS-SOL-05 | Lock Service Access Door Switch 1 | 24Vdc | 016 | 19 | DO19+ | X-DO 24 01 | X-CB 009 01 | 19a | EXTERNAL | B10E-PS-DS-07 | Grey | 0.75mm² H05Z-K | 016/DO19+ | X-DS07 | 7 | DO1 | 0
[5 empty] | DO19- |  |  | 19b |  |  | White | 0.75mm² H05Z-K | 016/DO19- | X-DS07 | 8
B10E-PS-SOL-06 | Lock Service Access Door Switch 2 | 24Vdc | 016 | 20 | DO20+ | X-DO 24 01 | X-CB 009 01 | 20a | EXTERNAL | B10E-PS-DS-08 | Grey | 0.75mm² H05Z-K | 016/DO20+ | X-DS08 | 7 | DO1 | 0
[5 empty] | DO20- |  |  | 20b |  |  | White | 0.75mm² H05Z-K | 016/DO20- | X-DS08 | 8
SPDO-016/21 | Wired Spare Output | 24Vdc | 016 | 21 | DO21+ | X-DO 24 01 | X-CB 009 01 | 21a |  |  | Grey | 0.75mm² H05Z-K | 016/DO21+ | X-SPDO | 39 | DO1 | 0
[5 empty] | DO21- |  |  | 21b |  |  | White | 0.75mm² H05Z-K | 016/DO21- | X-SPDO | 40
SPDO-016/22 | Wired Spare Output | 24Vdc | 016 | 22 | DO22+ | X-DO 24 01 | X-CB 009 01 | 22a |  |  | Grey | 0.75mm² H05Z-K | 016/DO22+ | X-SPDO | 41 | DO1 | 0
[5 empty] | DO22- |  |  | 22b |  |  | White | 0.75mm² H05Z-K | 016/DO22- | X-SPDO | 42
SPDO-016/23 | Wired Spare Output | 24Vdc | 016 | 23 | DO23+ | X-DO 24 01 | X-CB 009 01 | 23a |  |  | Grey | 0.75mm² H05Z-K | 016/DO23+ | X-SPDO | 43 | DO1 | 0
[5 empty] | DO23- |  |  | 23b |  |  | White | 0.75mm² H05Z-K | 016/DO23- | X-SPDO | 44
SPDO-016/24 | Wired Spare Output | 24Vdc | 016 | 24 | DO24+ | X-DO 24 01 | X-CB 009 01 | 24a |  |  | Grey | 0.75mm² H05Z-K | 016/DO24+ | X-SPDO | 45 | DO1 | 0
[5 empty] | DO24- |  |  | 24b |  |  | White | 0.75mm² H05Z-K | 016/DO24- | X-SPDO | 46

## OVERVIEW
Beamline | B10E | HeXI | [5 empty] | SUMMARY: | AI | AO | DI | DO | BUS | CPU | COM | SPR
[8 empty] | TOTAL MODULES: | 1 | 0 | 3 | 4 | 0 | 2 | 2 | 6
[8 empty] | TOTAL IO: | 32 | 0 | 96 | 96 | 0 | 0 | 0 | 0
[8 empty] | TOTAL USED: | 19 | 0 | 66 | 96
[8 empty] | TOTAL SPARE | 13 | 0 | 30 | 0
[8 empty] | % SPARE | 40.62% |  | 31.25% | 0%
Chassis | 0
| SLOT | MODULE | Description | TYPE | Channels | Chassis & Slot | SHEET NAME
| 1 | X-CPU_31 | Processor 31 | CPU | 0 | 001
| 2 | X-CPU_31 | Processor 31 | CPU | 0 | 002
| 3 | X-COM_01 | Communications | COM | 0 | 003
| 4 | X-COM_01 | Communications | COM | 0 | 004
| 5 | X-AI_32_02 | Analogue Input 32 Channels | AI | 32 | 005 | 005_AI |  | 19
| 6 | X-DI_32_05 | Digital Input 32 Channels | DI | 32 | 006 | 006_DI |  |  |  | 1
| 7 | X-DI_32_05 | Digital Input 32 Channels | DI | 32 | 007 | 007_DI |  |  |  | 32
| 8 | X-DI_32_05 | Digital Input 32 Channels | DI | 32 | 008 | 008_DI |  |  |  | 33
| 9 | X-SPARE | Spare Slot | SPR | 0 | 009
| 10 | X-SPARE | Spare Slot | SPR | 0 | 010
| 11 | X-SPARE | Spare Slot | SPR | 0 | 011
| 12 | X-SPARE | Spare Slot | SPR | 0 | 012
| 13 | X-DO_24_01A | Digital Output 24 Channels | DO | 24 | 013 | 013_DO |  |  |  |  | 24
| 14 | X-DO_24_01A | Digital Output 24 Channels | DO | 24 | 014 | 014_DO |  |  |  |  | 24
| 15 | X-DO_24_01A | Digital Output 24 Channels | DO | 24 | 015 | 015_DO |  |  |  |  | 24
| 16 | X-DO_24_01A | Digital Output 24 Channels | DO | 24 | 016 | 016_DO |  |  |  |  | 24
| 17 | X-SPARE | Spare Slot | SPR | 0 | 017
| 18 | X-SPARE | Spare Slot | SPR | 0 | 018
Chassis | 1
| SLOT | MODULE | Description | TYPE | Channels | Chassis & Slot
| 1 |  | 0 | 0 | 0 | 101
| 2 |  | 0 | 0 | 0 | 102
| 3 |  | 0 | 0 | 0 | 103
| 4 |  | 0 | 0 | 0 | 104
| 5 |  | 0 | 0 | 0 | 105
| 6 |  | 0 | 0 | 0 | 106
| 7 |  | 0 | 0 | 0 | 107
| 8 |  | 0 | 0 | 0 | 108
| 9 |  | 0 | 0 | 0 | 109
| 10 |  | 0 | 0 | 0 | 110
| 11 |  | 0 | 0 | 0 | 111
| 12 |  | 0 | 0 | 0 | 112
| 13 |  | 0 | 0 | 0 | 113
| 14 |  | 0 | 0 | 0 | 114
| 15 |  | 0 | 0 | 0 | 115
| 16 |  | 0 | 0 | 0 | 116
| 17 |  | 0 | 0 | 0 | 117
| 18 |  | 0 | 0 | 0 | 118

## DATA
Module Ref | Description | Type | Channels
X-SB_01 | System Bus | BUS | 0
X-CPU_01 | Processor 01 | CPU | 0
X-CPU_31 | Processor 31 | CPU | 0
X-COM_01 | Communications | COM | 0
X-SPARE | Spare Slot | SPR | 0
X-AI_32_02 | Analogue Input 32 Channels | AI | 32
X-AO_16_01 | Analogue Output 16 Channels | AO | 16
X-DI_32_05 | Digital Input 32 Channels | DI | 32
X-DO_24_01A | Digital Output 24 Channels | DO | 24