# 3 · Test procedure — every step

*A functional-test walkthrough of the B10E PSS, written so a junior engineer can follow it exactly. Each test states: purpose → setup → action → expected result, and gives the simulator commands so you can rehearse it before ever touching real plant.*

Two kinds of "test" — don't mix them up * Functional / proof test (this document): prove each Safety Function does   what the Cause & Effect matrix says (right cause → right effect). That is what   the simulator reproduces. * Hardware service test: measuring 24 V/5 V rails, checking crimps, fans,   earth, module seating, etc. That is a *separate*, generic HIMA field-service   checklist and is not part of this project's logic. (An old generic copy of   that form was in the repo's history and has been removed.)

Golden rule for real plant: only do these on a system that has been formally taken out of service / under a permit to work, with the beam interlock isolated as your site procedure requires. Tripping a live safety function on a running machine is never a "quick check".

__________________________________________________

## 3.0 Before you start (every test)

Record the starting state: in the simulator type state; on real plant, read

and save the diagnostic/event list first (before you touch anything).

Confirm the healthy baseline: all doors closed, keys IN, no latched trips,

annunciator OPEN/OPEN_READY.    ``    python3 pss_cli.py    pss> state          # expect HUTCH STATE: OPEN_READY, all contactors off (safe), no TRIPS

Know your reset: each latched function has its own reset button

(reset BOB, reset RDMN, reset GAS, reset OR).

__________________________________________________

## TEST 1 — SIF-08 Beam-Off Buttons (1oo7 emergency stop)

Purpose: any single beam-off button must remove the beam, and the trip must latch until reset.

Setup: get to BEAM_ON.

pss> search                 # macro: full valid search + beam enable -> BEAM_ON
pss> state                  # confirm: CON01-05 ON, annunciator BEAM ON

Action & expected result:

| Step | Action | Expected |
| --- | --- | --- |
| 1 | bob 3 (press beam-off button 3) | all electron-source CON01-05 and RF CON06-10 go off; state leaves BEAM_ON; TRIPS: SIF-08 ... (latched) |
| 2 | bob 3 up (release the button) | contactors stay off (latched) — releasing does not restart the hazard |
| 3 | reset BOB | latch clears (latch=off) |
| 4 | repeat for buttons 1–8 | each one alone must trip (1oo7) |

Why it matters: this is the operator's emergency stop; it must work from any one of the 8 stations and must never auto-restart.

__________________________________________________

## TEST 2 — SIF-01 General Access Door (2oo3)

Purpose: opening the general door with beam on isolates the source; and prove the 2oo3 voting (1 switch alone must NOT trip — that would be a nuisance trip).

Setup: search → BEAM_ON.

| Step | Action | Expected |
| --- | --- | --- |
| 1 | door GADC01 open | no trip — only 1 of 3 switches (2oo3 tolerates one) |
| 2 | door GADC02 open | now 2 of 3 → CON01-03 off, drops out of BEAM_ON, SEARCHED_AND_LOCKED latch broken |
| 3 | door GADC01 close + door GADC02 close | doors closed again, but beam does not come back — you must run a new search |
| 4 | search | beam returns only after a fresh, valid search |

Real-plant note: the 2oo3 means one failed/disconnected door switch will not shut the beamline down on its own (availability) — but two will (safety).

__________________________________________________

## TEST 3 — SIF-13 General Access Gate (2oo3, 200 ms)

Purpose: the gate is split from the door (Rev 4 of the C&E) and drops the RF contactors CON06-08 with a 200 ms delay.

Setup: search → BEAM_ON.

| Step | Action | Expected |
| --- | --- | --- |
| 1 | door GADC04 open | 1 of 3 gate switches — no trip |
| 2 | door GADC05 open | 2oo3 gate → CON06-08 off (RF power) |

__________________________________________________

## TEST 4 — SIF-02 Service Access Door (2oo3 + 1oo2)

Setup: search → BEAM_ON.

| Step | Action | Expected |
| --- | --- | --- |
| 1 | door SADC01 open then door SADC02 open | group C 2oo3 → source contactors off |
| 2 | reset by closing + new search; then door SADC04 open | group D is 1oo2 — this single one trips |

__________________________________________________

## TEST 5 — SIF-09 Radiation Monitors (1oo2, latched)

Purpose: a high radiation reading removes the hazard and latches.

Setup: search → BEAM_ON.

| Step | Action | Expected |
| --- | --- | --- |
| 1 | bob … no — use the radiation monitor: open the CLI and set demand via state; in this build use the door/analog commands. For RDMN, use the scenario or python3 -c snippet below. | — |

Run it directly:

python3 -c "from pss_sim import *; p=PSS();
import scenarios as s; s.do_full_search(p);
p.demand['RDMN01']=True; p.scan();
print('CON01 =', p.outputs()['CON01'], '(expect False)');
print('latched =', p.latch_rdmn, '(expect True)')"

Expected: CON01 = False, latched = True. Clear with reset RDMN (after the monitor returns to normal). 1oo2: either monitor alone trips.

__________________________________________________

## TEST 6 — SIF-11 Oxygen Depletion (1oo4)

Purpose: any one oxygen monitor reading low closes the LN₂ valve and raises the O₂ alarm.

Setup: any state (this function is independent of the search).

| Step | Action | Expected |
| --- | --- | --- |
| 1 | ai OXMON02 18 (monitor 2 reads 18 % O₂, below 19.5 %) | LN2 valve CLOSES (SDVLN2 off); O₂ traffic-lights RED; alarm beacon |
| 2 | ai OXMON02 20.9 (restore) then reset GAS | valve re-opens, lights green |
| 3 | try each of OXMON01–04 | any one alone trips (1oo4) |

__________________________________________________

## TEST 7 — SIF-03 Radiation-present door interlock (2oo3, 20 s, Open/Reset)

Purpose: you must not be able to unlock the doors while the source is still energised; and even after it reads zero there is a 20 s confirm and an Open/Reset button press before doors release.

| Step | Action | Expected |
| --- | --- | --- |
| 1 | ai IT01 12 then ai IT02 12 | 2oo3 current "present" → radiation_present = YES; door locks held ON |
| 2 | ai IT01 3 ai IT02 3 (back to ~0) then wait 5 | Open/Reset LED still off (only 5 s of the 20 s confirm) |
| 3 | wait 20 | Open/Reset LED comes ON (source confirmed zero for ≥20 s) |
| 4 | reset OR | doors may now unlock; hutch returns toward OPEN |

__________________________________________________

## TEST 8 — SIF-10 Electron-Source Enable Key

| Step | Action | Expected |
| --- | --- | --- |
| 1 | search → BEAM_ON | RF contactors CON06-10 ON |
| 2 | key KEY03 off | SIF-10 → RF/source isolation (key_off trip) |
| 3 | key KEY03 on | does not auto-restart — a key is not a reset; run a new search |

__________________________________________________

## TEST 9 — The SEARCH itself (SIF-04/05/06)

This is Test of the sequence and its interlocks. Work through 02_SEARCH_SEQUENCE.md §2.6. Specifically prove each abort:

| Case | How to provoke | Expected |
| --- | --- | --- |
| Wrong order | card, wait 10, asb1 (before lcrx) | ABORT "out-of-order" |
| Too fast | card, wait 2, lcrx | ABORT "too fast (<5s)" |
| Too slow | card, wait 70, lcrx | ABORT "too slow (>60s)" |
| Door during search | card, wait 10, lcrx, door GADC01 open… GADC02 | ABORT "door opened/hazard during search" |
| Can't declare searched with door open | run to ASB4, door GADC01 open+GADC02, asbf | ASBF refused / aborts (SIF-06 not satisfied) |

__________________________________________________

## 3.x Test record template

For each test, record:

SIF / Test no.: ____    Date: ____    Engineer: ____
Pre-state recorded?  Y / N
Cause applied:        ___________________________
Expected effect:      ___________________________
Observed effect:      ___________________________
Latched? reset OK?    Y / N
PASS / FAIL:          ____      Notes: __________

Run the whole functional set automatically at any time with:

python3 scenarios.py     # 7 scenarios, PASS/FAIL each, must be 7/7