# 4 · SILworX offline‑simulation test procedure

*This is the main "do this" document. You run it in HIMA SILworX offline simulation (the PLC program running on your PC, with no real hardware). For each safety function it tells you, in plain steps: which signal to force (set by hand), which signal to watch, and what should happen. Every tag (signal name) has a short description; the full list is in document 00 (the tag glossary).*

Everything here comes from the real program file program.pdf (project C15862H-BL10E, configuration BL10E_HeXI [400], SILworX v16.0.0 R3326). The searchable text of all 713 pages is in data/program_extracted.txt.

__________________________________________________

## 0 · Set‑up and the rules you must know first

### 0.1 Start the offline simulation

Open the project and select the Resource `BL10E_HeXI [400]` (the controller).

Generate the code, then start Offline Simulation on that resource.

Open a logic page (for example Library/SIF/B10E-SIF-01). In simulation the

wires on the page show live TRUE/FALSE values, so you can watch the logic work.

Open the Force editor (or a Watch page). "Forcing" means setting a signal to a

value by hand. Add the tags listed in each test.

### 0.2 The two big rules

Rule 1 — you are the field. In offline simulation there is no real wiring, so a sensor input just sits at its starting value until *you* force it. Forcing an input is like operating the real plant.

A trap that follows from Rule 1 — feedback does not follow outputs. When the PLC energises a lock output BL10E-PS-SOL-01 (the bolt solenoid that locks a door), the matching feedback input BL10E-PS-GADL-01 (the switch that senses the bolt is in) does not move by itself. On the real door the bolt moves the switch; in simulation you must force the feedback to copy that. This matters in the search (§4): if you do not force BL10E-PS-GADL-… and BL10E-PS-SADL-… (the door‑locked sensing switches) to 1 after the locks energise, the beam‑on permit BL10E-SIF-07_OUTPUT (the master "beam may come on" signal) never turns on, and the beam never comes on.

Rule 2 — OFF is the safe state ("de‑energise‑to‑trip"). Almost every output's safe state is OFF. So for most inputs the unsafe / "do something" value is `0`, and many internal signals are permissives — a permissive is 1 when everything is healthy and drops to 0 to trip. The one exception: the analogue trip flags BL10E-PS-IT/VT/OXMON‑0x_TRIP (the "limit reached" flags from the current, voltage and oxygen sensors) are the other way round — 1 means a limit was crossed.

### 0.3 Which way to force each signal (polarity)

*Tip: for a picture of which switch belongs to which door or gate, see the sketch at the top of document 00 (the glossary).*

| Signal (tag) | What it is (the exact device) | Healthy / normal | Unsafe value / action |
| --- | --- | --- | --- |
| BL10E-PS-GADC-01, -02, -03 | The three "closed" switches on the main personnel door | 1 = door shut | 0 = door open |
| BL10E-PS-GADC-04, -05, -06 | The three "closed" switches on the entrance gate | 1 = gate shut | 0 = gate open |
| BL10E-PS-SADC-01, -02, -03 | The three "closed" switches on the service door (first set, voted 2oo3) | 1 = shut | 0 = open |
| BL10E-PS-SADC-04, -05 | A second pair of "closed" switches on the service door (voted 1oo2) | 1 = shut | 0 = open |
| BL10E-PS-GADL-01, -02 | The two "locked" switches that sense the main‑door bolt | 1 = locked | 0 = not locked |
| BL10E-PS-GADL-04, -05 | The two "locked" switches that sense the gate bolt | 1 = locked | 0 = not locked |
| BL10E-PS-SADL-01, -02 | The two "locked" switches that sense the service‑door bolt | 1 = locked | 0 = not locked |
| BL10E-PS-KEY-01 | Electron‑source enable key at the ZCP (Zone Control Panel, by the hutch) | 1 = on | 0 = off |
| BL10E-PS-KEY-02 | Hutch enable key (the one needed to start a search) | 1 = on | 0 = off |
| BL10E-PS-KEY-03 | Electron‑source enable key at the equipment rack (cabinet / rack room, away from the hutch) | 1 = on | 0 = off |
| BL10E-PS-SCR-01 | Search‑card reader at the door | 1 = card in | 0 = no card |
| BL10E-PS-BOB-01:A/:B … BOB-08:A/:B | The 8 emergency Beam‑Off Buttons; each has two channels :A and :B | 1 = not pressed | 0 = pressed |
| BL10E-PS-ASB-01, -02, -03, -04 | The four area‑search buttons, pressed in order during the walk | 0 = idle | a press = 0→1 |
| BL10E-PS-ASBF-01 | The final area‑search button, by the exit door | 0 = idle | a press = 0→1 |
| BL10E-PS-LCRx-01 | Light curtain across the doorway | 1 = clear | 0 = beam broken |
| BL10E-PS-OR-01 | The Open/Reset button | 0 = idle | a press = 0→1 |
| BL10E-PS-IT-01, -02, -03_TRIP (see §0.4) | Trip flags from the source current sensors | force 0 = no current | force 1 = current present |
| BL10E-PS-VT-01, -02, -03_TRIP (see §0.4) | Trip flags from the source voltage sensors | force 0 = no voltage | force 1 = voltage present |
| BL10E-PS-OXMON-01…-04_TRIP (see §0.4) | Trip flags from the four oxygen sensors | force 0 = air OK | force 1 = oxygen low |
| BL10E-PS-RDMND-01, -02 | Radiation dose sensors | healthy | trip value |
| BL10E-PS-RDMNR-01, -02 | Radiation dose‑rate sensors | healthy | trip value |
| BL10E-PS-IOC-01-BOB:RESET | Control‑room reset for the beam‑off‑button latch | 0 = idle | a press = 0→1 |
| BL10E-PS-IOC-01-RDMN:RESET | Control‑room reset for the radiation latch | 0 = idle | a press = 0→1 |
| BL10E-PS-IOC-01-GAS:RESET | Control‑room reset for the oxygen latch | 0 = idle | a press = 0→1 |
| BL10E-PS-IOC-01-SYS:RESET | Control‑room reset for general system latches | 0 = idle | a press = 0→1 |
| OUTPUT BL10E-PS-CON-01:EN … CON-05:EN | Commands to the contactors feeding the electron source | — | 1 = on (hazard live), 0 = safe |
| OUTPUT BL10E-PS-CON-06:EN … CON-08:EN | Commands to the 3‑phase RF contactors | — | 1 = on, 0 = safe |
| OUTPUT BL10E-PS-CON-09:EN, CON-10:EN | Commands to the 1‑phase RF drive contactors | — | 1 = on, 0 = safe |
| OUTPUT BL10E-PS-SOL-01, -02 | The bolt solenoids that lock the main door | — | 1 = locked, 0 = unlocked |
| OUTPUT BL10E-PS-SOL-03, -04 | The bolt solenoids that lock the gate | — | 1 = locked, 0 = unlocked |
| OUTPUT BL10E-PS-SOL-05, -06 | The bolt solenoids that lock the service door | — | 1 = locked, 0 = unlocked |

### 0.4 Important: the analogue set‑points are fixed "fail‑safe" numbers

The PLC turns each 4–20 mA sensor into a trip flag using a limit block. The level at which it trips is a set‑point tag …_SP. In this program the as‑built set‑points are:

| Set‑point tag | Value | Block | What it does as shipped |
| --- | --- | --- | --- |
| BL10E-PS-OXMON-01..04_SP (oxygen trip level) | 25.0 | X_LimL (trips when the reading goes below the set‑point) | 25 is the top of range, so the oxygen trip is always active |
| BL10E-PS-IT-01..03_SP, VT-01..03_SP (source current/voltage trip level) | 0.0 | X_LimH (trips when the reading goes above the set‑point) | 0 means "source present" is always active |
| all …_HYST (the small dead‑band) | 0.2 | — | — |

Two things follow:

These are deliberate fail‑safe placeholders — until the system is commissioned with

real numbers, the analogue functions sit in their tripped (safe) state.

They are marked `Constant`, so in offline simulation **you cannot force …_SP or

…_HYST**, and forcing the raw reading (e.g. BL10E-PS-IT-01 = 3.9) can never clear the    trip (3.9 is still above 0.0).

So you have two ways to test the analogue functions:

Way A (easy, no code change): force the trip flag directly — set

BL10E-PS-OXMON-01..04_TRIP, IT-01..03_TRIP, VT-01..03_TRIP (the "limit reached"   flags) to 0 for healthy, or to 1 to fake a trip. Forcing overrides what the program   writes, so everything downstream behaves exactly as designed.

Way B (to test the limit blocks themselves): edit the …_SP starting values in the

global‑variable editor (for example OXMON-01_SP = 19.5, IT-01_SP = 6.0), regenerate   the code, restart the simulation — now forcing the raw reading works. Put the values back   afterwards.

### 0.5 The timers run on the simulation clock

The program uses several timers. In offline simulation they count down in real (simulated) time, so you sometimes have to wait.

| Timer (tag) | Value | What it is, in plain words |
| --- | --- | --- |
| MAX_SEARCH_TIME | 180 s (3 min) | The whole search must finish within 3 minutes, or it cancels. |
| per‑step window (T1-T2_TIMER…T6-T7_TIMER) | 5–60 s | Between each search button: wait at least 5 s (so nobody can rush the search) but no more than 60 s. |
| BEAM_DELAY_TIMER_TIME | 180 s (3 min) | After the search, the system waits 3 minutes (with warning lights/sirens) before the beam may come on. |
| DOOR_UNLOCK_DELAY | 20 s | After the source reads zero, wait 20 s to be sure before doors may unlock. |
| LIGHT_CURTAIN_DELAY | 2 s | A 2‑second pause after someone enters before the light curtain starts watching for extra people. |
| RESET_DELAY_TIMER | 60 s | A 1‑minute wait before the system returns to fully "Open". |
| E_SOURCE_TIME | 120 s (2 min) | How long the source must read off before the alarm screen treats it as truly dead. |

### 0.6 Keep a test record

For every test, write down: the starting state, what you forced, what you watched, what happened, whether it latched (stuck on until reset), and PASS/FAIL. A blank form is at the end (§9).

__________________________________________________

## 1 · Set the healthy starting point (do this before every test)

Why: every test must start from a known, safe plant — all doors shut, keys in, nothing pressed, sensors healthy. The program shows this as STATUS-OPEN_READY = 1 (the "ready to start a search" state).

Step 1 — force every input to the value in the last column. Each tag is listed on its own so you can see exactly what it is.

| Tag | What it is (the exact device) | Force to |
| --- | --- | --- |
| BL10E-PS-GADC-01, -02, -03 | The three closed‑switches on the main personnel door | 1 (door shut) |
| BL10E-PS-GADC-04, -05, -06 | The three closed‑switches on the entrance gate | 1 (gate shut) |
| BL10E-PS-SADC-01, -02, -03 | The service door closed‑switches (first set) | 1 (shut) |
| BL10E-PS-SADC-04, -05 | The service door closed‑switches (second set) | 1 (shut) |
| BL10E-PS-KEY-01 | Electron‑source enable key at the ZCP (Zone Control Panel, by the hutch) | 1 (on) |
| BL10E-PS-KEY-02 | Hutch enable key (needed to start a search) | 1 (on) |
| BL10E-PS-KEY-03 | Electron‑source enable key at the equipment rack (cabinet / rack room, away from the hutch) | 1 (on) |
| BL10E-PS-BOB-01:A/:B … BOB-08:A/:B | All 16 channels of the 8 beam‑off buttons | 1 (not pressed) |
| BL10E-PS-LCRx-01 | The light curtain across the doorway | 1 (clear) |
| BL10E-PS-ASB-01, -02, -03, -04 | The four area‑search buttons | 0 (idle) |
| BL10E-PS-ASBF-01 | The final area‑search button | 0 (idle) |
| BL10E-PS-SCR-01 | The search‑card reader | 0 (no card) |
| BL10E-PS-OR-01 | The Open/Reset button | 0 (idle) |
| BL10E-PS-GADL-01, -02 | The main‑door "locked" switches (locks not on yet) | 0 (not locked) |
| BL10E-PS-GADL-04, -05 | The gate "locked" switches (locks not on yet) | 0 (not locked) |
| BL10E-PS-SADL-01, -02 | The service‑door "locked" switches (locks not on yet) | 0 (not locked) |
| BL10E-PS-RDMND-01, -02 | The radiation dose sensors | 0 (healthy) |
| BL10E-PS-RDMNR-01, -02 | The radiation dose‑rate sensors | 0 (healthy) |
| BL10E-PS-OXMON-01…-04_TRIP | The four oxygen trip flags (Way A, §0.4) | 0 (air OK) |
| BL10E-PS-IT-01, -02, -03_TRIP | The source current trip flags (Way A, §0.4) | 0 (no current) |
| BL10E-PS-VT-01, -02, -03_TRIP | The source voltage trip flags (Way A, §0.4) | 0 (no voltage) |

*(If you use Way B from §0.4 instead, force the raw readings: IT-0x = 3.9, VT-0x = 3.9, OXMON-0x = 20.9.)*

Step 2 — press each control‑room reset once (force 0→1→0) to clear any latch left from power‑up:

| Tag | What it resets |
| --- | --- |
| BL10E-PS-IOC-01-BOB:RESET | the beam‑off‑button latch |
| BL10E-PS-IOC-01-RDMN:RESET | the radiation latch |
| BL10E-PS-IOC-01-GAS:RESET | the oxygen latch |

Step 3 — check you are at the healthy start. You should see:

| Watch this | Expect | Meaning |
| --- | --- | --- |
| STATUS-OPEN_READY | 1 | the hutch is ready to start a search |
| BL10E-PS-ANNOPN-01:A/:B | 1 | the "OPEN" sign is on |
| BL10E-PS-CON-01:EN … CON-10:EN | all 0 | every hazard is off |
| BL10E-PS-SOL-01 … SOL-06 | all 0 | every door is unlocked |
| BL10E-SIF-01_TRIP … SIF-13_TRIP | at healthy value (mostly 1) | every safety function is healthy |

__________________________________________________

## 2 · Input‑layer tests (how a sensor becomes a trip)

### 2.1 An analogue sensor → its trip flag *(needs Way B from §0.4)*

Idea: each 4–20 mA sensor reading is compared with its set‑point by a limit block — X_LimH (HIMA's "trip when above" block) for current/voltage, X_LimL ("trip when below") for oxygen — which produces the trip flag …_TRIP.

This test only works if you use Way B (edit the set‑points), because the set‑points are Constant. Set OXMON-01_SP = 19.5 and IT-01_SP = 6.0, regenerate, restart. If you stay on Way A, skip this test — the safety‑function behaviour is fully covered by forcing …_TRIP in §3.

Open the Analogue Inputs logic (pages 184–187).

Force BL10E-PS-OXMON-01 = 20.9 (a healthy oxygen reading). Watch

OXMON-01_TRIP = 0.

Force BL10E-PS-OXMON-01 = 18.0 (below the 19.5 set‑point). Watch

OXMON-01_TRIP turn 1 (a low‑oxygen trip).

Force BL10E-PS-OXMON-01 = 19.6 (just above the set‑point). Watch that it

stays tripped until the reading clears the set‑point *plus* the dead‑band —    that is the hysteresis at work.

Force BL10E-PS-IT-01 = 12.0 (a high source‑current reading). Watch

IT-01_TRIP turn 1 (a high trip).

Proves: you can follow any analogue sensor from its raw reading to its trip flag.

### 2.2 Two‑channel inputs and the "discrepancy" alarm

Idea: the beam‑off buttons (and some lamps) use two wires, :A and :B, that are checked against each other so a single broken wire cannot fake a healthy button. If :A and :B disagree for too long, a 2In_Discrepency_Alarm block raises a fault alarm — that is different from a safety trip.

Force BL10E-PS-BOB-05:A = 0 (channel A of beam‑off button 5 "pressed") while

leaving BL10E-PS-BOB-05:B = 1 (channel B "not pressed").

Watch the beam‑off function BL10E-SIF-08_TRIP (the "no button pressed"

permissive) behave per design, and the BOB‑05 discrepancy alarm appear in    the Alarms logic (page 171).

Set both channels back to 1 and reset.

Proves: a wiring fault is detected and is handled separately from a real trip.

__________________________________________________

## 3 · Safety‑function (SIF) tests — one at a time

A SIF is one independent safety function. Re‑do the §1 starting point between tests. Each test names the page to open, the tag to force, the signal to watch, and the result to expect.

### SIF‑01 — Main personnel door open → cut the source (page 291)

What it protects: if the main door opens, the electron source must switch off — radiation must never be on with the door open. How it is built: the three door‑closed switches BL10E-PS-GADC-01/02/03 go into a 2oo3 voter (HIMA block X_2oo3_B; "2oo3" means at least 2 of the 3 must say "open" before it counts). The voter output is combined (AND) with the beam‑on permit BL10E-SIF-07_OUTPUT to make BL10E-SIF-01_TRIP (a permissive: 1 = door OK).

Get to STATUS-BEAM_ON (do the §4 search first) or just use the §1 start point.

Force BL10E-PS-GADC-01 = 0 (one door switch says "open"). Expect: the voter

stays healthy and BL10E-SIF-01_TRIP stays 1 — no trip (2oo3 tolerates one    switch). After a short delay the voter's Dev output flags the disagreement.

Also force BL10E-PS-GADC-02 = 0 (now 2 of 3 say "open"). Expect:

BL10E-SIF-01_TRIP turns 0, and the source contactors BL10E-PS-CON-01:EN,    CON-02:EN, CON-03:EN (and CON-10:EN, same memory group, page 267) turn 0    — the source is isolated.

Set both switches back to 1. Expect: the contactors stay 0 — see the

memory‑latch test in §5; you must run a fresh search to get the hazard back.

### SIF‑13 — Gate open → cut the RF (page 382)

What it protects: the entrance gate is separate from the door; opening it cuts the RF supply, with a small 200 ms delay (to ride through switch bounce on a moving gate). How it is built: the three gate switches BL10E-PS-GADC-04/05/06 go into a 2oo3 voter, combined with BL10E-SIF-07_OUTPUT (beam‑on permit) → BL10E-SIF-13_TRIP.

Force BL10E-PS-GADC-04 = 0 (one gate switch open). Expect: no trip.

Also force BL10E-PS-GADC-05 = 0 (2 of 3). Expect: BL10E-SIF-13_TRIP turns

0; after ~200 ms the RF contactors BL10E-PS-CON-06:EN, CON-07:EN, CON-08:EN    (and CON-09:EN, same group) turn 0.

### SIF‑02 — Service door open → cut the source (page 297)

What it protects: the service/maintenance door is a second way in. How it is built: the three service‑door switches BL10E-PS-SADC-01/02/03 go into a 2oo3 voter; this is OR‑ed with a 1oo2 pair BL10E-PS-SADC-04 and SADC-05 ("1oo2" means either one is enough). The result, combined with BL10E-SIF-07_OUTPUT, makes BL10E-SIF-02_TRIP.

Test the 2oo3 side: force BL10E-PS-SADC-01 = 0, then SADC-02 = 0.

Expect: BL10E-SIF-02_TRIP turns 0; source contactors CON-01/02/03:EN → 0.

Test the 1oo2 side: from the §1 start point, force only BL10E-PS-SADC-04 = 0.

Expect: it trips on its own (1oo2 needs just one).

### SIF‑03 — "Is the source really off?" / permission to unlock (page 303)

What it protects: doors may only unlock once the source is proven dead — measured two ways, current and voltage — and held off for 20 s, then a person must press a button. This stops doors unlocking on a brief dip or one faulty sensor. How it is built: a 2oo3 voter on the current trips BL10E-PS-IT-01/02/03_TRIP and another on the voltage trips BL10E-PS-VT-01/02/03_TRIP; a memory (RS latch); an on‑delay timer DOOR_UNLOCK_DELAY = 20 s; the Open/Reset button BL10E-PS-OR-01; and a lamp BL10E-PS-OR-01:LED ("you may press now") → BL10E-SIF-03_OUTPUT.

Using Way A (force the trip flags):

Force BL10E-PS-IT-01_TRIP = 1 and IT-02_TRIP = 1 (2 of 3 current sensors say

"source live"). Expect: "source present" wins, the door locks SOL-0x are    held on (1), and the lamp BL10E-PS-OR-01:LED = 0.

Force IT-01_TRIP = 0 and IT-02_TRIP = 0 (source now reads zero). Wait **less

than 20 s. Expect:** OR-01:LED is still 0 (the 20 s check is running).

Wait until 20 s have passed. Expect: OR-01:LED turns 1.

Press BL10E-PS-OR-01 (force 0→1). Expect: BL10E-SIF-03_OUTPUT allows

unlocking; the system heads back toward "Open" (after the 60 s RESET_DELAY_TIMER).

Repeat steps 1–4 using VT-01_TRIP/VT-02_TRIP (the voltage sensors) — same result.

### SIF‑05 — Permission to start a search (page 344)

What it protects: a search may only begin with the right authority, the service doors shut, and no stop button latched. Each item is a hard condition — remove any one and the search must refuse to start (these are the negative tests). How it is built: an AND of BL10E-PS-SCR-01 (search card in), KEY-01 and KEY-02 (both enable keys on), the 1oo2 pair SADC-04 and SADC-05, the 2oo3 voter on SADC-01/02/03, and BL10E-SIF-08_TRIP (no beam‑off button) → BL10E-SIF-05_START.

From the §1 start point, for each row force the listed item, then present the card BL10E-PS-SCR-01 = 1:

| Block this | Force | Expect |
| --- | --- | --- |
| nothing (control) | just SCR-01 = 1 | BL10E-SIF-05_START = 1, then STATUS-START_SEARCH = 1 — a search starts ✔ |
| key 1 missing | BL10E-PS-KEY-01 = 0 | SIF-05_START stays 0 — no search |
| key 2 missing | BL10E-PS-KEY-02 = 0 | stays 0 |
| service door open | BL10E-PS-SADC-04 = 0 | stays 0 |
| beam‑off latched | press+release a beam‑off button without resetting | stays 0 until you press IOC-01-BOB:RESET |

### SIF‑06 — Proof the search may finish (page 350)

What it protects: the final search button only counts if every door and gate is shut at that moment. How it is built: a 2oo3 voter on BL10E-PS-GADC-01/02/03 (door) AND a 2oo3 voter on GADC-04/05/06 (gate) → BL10E-SIF-06_TRIP.

During the search (§4), at the STATUS-ASB4 step, force BL10E-PS-GADC-01 = 0 and

GADC-02 = 0 (open the door). Press BL10E-PS-ASBF-01 (the final button).    Expect: the final step is refused (BL10E-SIF-06_TRIP = 0, no STATUS-STANDBY).

Set the door switches back to 1, press ASBF-01 again. Expect: now it moves to

STATUS-STANDBY.

### SIF‑07 — Beam‑on permit / proof the locks really engaged (page 356)

What it protects: locked doors must be proven (by the lock switches, not just the command), and then a 180 s "radiation imminent" warning gives anyone inside a last chance to hit a stop button. How it is built: an AND of the door‑locked switches BL10E-PS-GADL-01, GADL-02, GADL-04, GADL-05, SADL-01, SADL-02, plus BL10E-SIF-06_TRIP (search complete), feeding a 180 s timer BEAM_DELAY_TIMER and a memory → BEAM_DELAY_TIMER_END and the master permit BL10E-SIF-07_OUTPUT.

Positive test: during §4 after the final button, force the six lock switches

GADL-01/02/04/05 and SADL-01/02 to 1 (copying the bolts going in). Wait 180 s.    Expect: BEAM_DELAY_TIMER_END = 1 and BL10E-SIF-07_OUTPUT = 1 (beam may come on).

Negative test: repeat, but leave `SADL-02 = 0` (one lock fails to engage).

Expect: BL10E-SIF-07_OUTPUT stays 0 and the beam never comes on.

### SIF‑08 — Beam‑Off Buttons (emergency stop) (page 363)

What it protects: the emergency stop. Pressing any one of the 8 buttons (this is "1oo7" — one out of many) cuts both the source and the RF, and unlocks the doors so people can get out. It latches (stays tripped): releasing the button must never restart the hazard — only a separate reset clears it. How it is built: each button's two channels BOB-0x:A and BOB-0x:B are AND‑ed; all buttons feed a memory (RS latch); the reset is BL10E-PS-IOC-01-BOB:RESET; the output is the permissive BL10E-SIF-08_TRIP.

Force BL10E-PS-BOB-03:A = 0 and BOB-03:B = 0 (press button 3, both channels).

Expect: BL10E-SIF-08_TRIP turns 0; contactors CON-01:EN, 02, 03, 06, 07, 08,    09, 10 all turn 0; locks SOL-0x turn 0 (instant unlock to escape).

Set both channels back to 1. Expect: BL10E-SIF-08_TRIP stays 0 (latched).

Press BL10E-PS-IOC-01-BOB:RESET (force 0→1→0). Expect: SIF-08_TRIP

returns to 1 (but the hazard stays off until a new search).

Repeat for buttons 1, 2, 4, 5, 6, 7, 8 — each one alone must trip (1oo7).

### SIF‑09 — Radiation sensors (page 368)

What it protects: if the radiation sensors read high, cut the hazard. Voting is 1oo2 (either sensor is enough — a real alarm must never be out‑voted). It latches. How it is built: the dose sensors BL10E-PS-RDMND-01/02 and dose‑rate sensors RDMNR-01/02 feed a memory (RS latch); the reset is BL10E-PS-IOC-01-RDMN:RESET; the output is BL10E-SIF-09_TRIP.

Force BL10E-PS-RDMND-01 to its trip value. Expect: BL10E-SIF-09_TRIP = 0;

source contactors CON-01/02/03:EN → 0 (and CON-10:EN).

Set it back to healthy. Expect: it stays tripped (latched).

Press BL10E-PS-IOC-01-RDMN:RESET. Expect: it clears.

Repeat with RDMNR-01, RDMND-02, RDMNR-02 (1oo2 — any one trips).

### SIF‑10 — Electron‑source enable key (page 372)

What it protects: a physical key is the permission to have the source/RF energisable at all. Voting is 1oo1 (one channel — the key is the law). Putting the key back is not a reset. How it is built: BL10E-PS-KEY-03 (the rack enable key) → BL10E-SIF-10_TRIP, which gates the contactors CON-04/05:EN (with SIF-08) and the RF group (page 267).

From STATUS-BEAM_ON, force BL10E-PS-KEY-03 = 0 (turn the key off). Expect:

BL10E-SIF-10_TRIP = 0; contactors CON-04:EN, CON-05:EN turn 0 (and watch which    RF contactors follow, page 267).

Force KEY-03 = 1 again. Expect: the hazard stays off — you recover only with a

new search.

### SIF‑11 — Oxygen monitors (page 377)

What it protects: cryogenic nitrogen can push out the air. Any one of four oxygen sensors reading low (this is "1oo4" — very sensitive) shuts the nitrogen valve and raises the oxygen alarm. It latches. How it is built: the four trip flags BL10E-PS-OXMON-01..04_TRIP feed a memory (RS latch); the reset is BL10E-PS-IOC-01-GAS:RESET; the output BL10E-SIF-11_TRIP closes the nitrogen valve BL10E-PS-SDVLN2, switches the oxygen beacons and the BL10E-PS-IND-01/02/03 traffic‑light indicators to red.

Force BL10E-PS-OXMON-02_TRIP = 1 (one oxygen sensor low). Expect: the valve

BL10E-PS-SDVLN2 = 0 (closed); the oxygen indicators go to alarm/red.

Force OXMON-02_TRIP = 0 again. Expect: it stays tripped (latched).

Press BL10E-PS-IOC-01-GAS:RESET. Expect: it clears.

Repeat for each of OXMON-01..04_TRIP (1oo4 — any one trips).

__________________________________________________

## 4 · The hutch search, step by step (the SFC, pages 326–338)

What it is: the search is a fixed walk‑through that proves nobody is left in the hutch. The program runs it as an SFC (a step‑by‑step state machine). One person sweeps the hutch pressing buttons in order. Two clocks watch them: the overall 180 s clock MAX_SEARCH_TIME, and a 5 s–60 s window between each step. Too fast means they did not really look; too slow means they lost control of the area.

Open these tags in a Watch page so you can see the search move: STATUS-OPEN_READY, STATUS-START_SEARCH, STATUS-HUTCH_ENTERED, STATUS-ASB1..ASB4, STATUS-STANDBY, STATUS-BEAM_ON (the search state), SEARCHED_AND_LOCKED (memory: "search done & locked"), SEARCH_TIMER_RUNNING and SEARCH_TIME_EXCEEDED (the 180 s clock), LIGHT_CURTAIN_MONITORING (curtain being watched), BEAM_DELAY_TIMER_END (the 180 s warning done), ABORT_SEARCH (search cancelled), the per‑step flags Tx-Ty_TIMER_TRIP_LOW/HIGH (too fast / too slow), and BL10E-SIF-05_START, SIF-06_TRIP, SIF-07_OUTPUT.

### 4.1 Walk it all the way to beam on

| Step | What you force | The state moves to | Also do / watch |
| --- | --- | --- | --- |
| 0 | the §1 start point | STATUS-OPEN_READY = 1 | — |
| T1 | BL10E-PS-SCR-01 = 1 (present the search card) | STATUS-START_SEARCH | BL10E-SIF-05_START = 1; service locks SOL-05/06 = 1; now force `SADL-01/02 = 1` (copy the bolts going in); the "RESTRICTED" sign ANNRES = 1; the 180 s clock starts |
| — | wait ≥ 5 s | — | the T1-T2_TIMER is running |
| T2 | pulse BL10E-PS-LCRx-01: 1→0→1 (one person steps through the light curtain) | STATUS-HUTCH_ENTERED | after 2 s LIGHT_CURTAIN_MONITORING = 1 (curtain now watched) |
| — | wait ≥ 5 s | — | — |
| T3 | pulse BL10E-PS-ASB-01: 0→1→0 (press search button 1) | STATUS-ASB1 | the button lamp ASB-01:LED = 1 |
| — | wait ≥ 5 s | — | — |
| T4 | pulse BL10E-PS-ASB-02 | STATUS-ASB2 | ASB-02:LED = 1 |
| — | wait ≥ 5 s | — | — |
| T5 | pulse BL10E-PS-ASB-03 | STATUS-ASB3 | ASB-03:LED = 1 |
| — | wait ≥ 5 s | — | — |
| T6 | pulse BL10E-PS-ASB-04 | STATUS-ASB4 | ASB-04:LED = 1; curtain watching ends |
| — | wait ≥ 5 s | — | — |
| T7 | pulse BL10E-PS-ASBF-01 (the final button; needs BL10E-SIF-06_TRIP = 1, i.e. all doors shut) | STATUS-STANDBY | general locks SOL-01..04 = 1; now force `GADL-01/02/04/05 = 1` ← *without this the search sticks here*; the "STANDBY" sign ANNSTB = 1; blue lights BLUEL-0x = 1; SEARCHED_AND_LOCKED = 1; the 180 s warning starts |
| — | wait 180 s | — | BEAM_DELAY_TIMER_END = 1, then BL10E-SIF-07_OUTPUT = 1 |
| T8 | (happens by itself) | STATUS-BEAM_ON | the "BEAM ON" sign ANNBON = 1; the beam‑on lamp BONI-01:A/:B = 1; the contactors CON-0x:EN = 1 (hazard live); the key KEY-01:SOL releases |

### 4.2 Prove the search cancels when it should (abort tests)

Each of these must send the search to a cancelled state (ABORT_SEARCH = 1) and back toward "Open":

| Cancel because | How to cause it | Watch |
| --- | --- | --- |
| wrong order | at STATUS-START_SEARCH, press ASB-01 before the light curtain | ABORT_SEARCH = 1 |
| too fast | press the next button less than 5 s after the last | the matching Tx-Ty_TIMER_TRIP_LOW = 1 → cancel |
| too slow | sit in a step more than 60 s | the matching Tx-Ty_TIMER_TRIP_HIGH = 1 → cancel |
| over the 180 s limit | drag the whole search past 180 s | SEARCH_TIME_EXCEEDED = 1 → cancel |
| curtain re‑broken | during T3–T6, pulse BL10E-PS-LCRx-01 = 0 | cancel while LIGHT_CURTAIN_MONITORING = 1 |
| key removed mid‑search | force BL10E-PS-KEY-01 = 0 (or KEY-02) before the final button | cancel |
| door opened mid‑search | force BL10E-PS-GADC-01 = 0 + GADC-02 = 0 | cancel |
| door open at the final button | open a door at STATUS-ASB4, then press ASBF-01 | final step refused (SIF-06_TRIP = 0) |

### 4.3 The enable‑key trap (page 337)

Idea: the key BL10E-PS-KEY-01 is held in place by a solenoid KEY-01:SOL during the search. At STATUS-BEAM_ON the program releases it so it can be moved to the rack. Removing it before the search finishes must cancel; removing it after release must not.

Mid‑search, force KEY-01 = 0 → the search cancels (already covered in §4.2).

Reach STATUS-BEAM_ON and watch KEY-01:SOL = 0 (the key is released).

__________________________________________________

## 5 · The "no silent restart" memory test (page 267) — the most important one

Idea: after any trip, simply clearing the cause must not bring the hazard back. The contactor logic combines the safety‑function permissives with SEARCHED_AND_LOCKED (the "search done & locked" memory) and STATUS-BEAM_ON through memory latches. The program page even says so:

*"If Search and Locked is broken, contactors 01, 02, 03, 06, 07, 08, 09 & 10 can not start again when tripped without going through a new search sequence."*

The contactor groups on page 267 are:

| Group | Contactors (the :EN command tags) | Held on by |
| --- | --- | --- |
| Source | CON-01, 02, 03, 10 | SIF-08 (no stop button) & SIF-01 (door) & SIF-02 (service door) & SIF-09 (radiation), plus SEARCHED_AND_LOCKED & STATUS-BEAM_ON |
| Gate / RF | CON-06, 07, 08, 09 | SIF-13 (gate) |
| Key | CON-04, 05 | SIF-10 (key) & SIF-08 |
| Door locks | SOL-01..06 | set when the search reaches each lock step, cleared at "Open" or by a stop button |

Reach STATUS-BEAM_ON (§4). Confirm the contactors CON-0x:EN = 1.

Cause any trip (for example press one beam‑off button). Expect: CON-0x:EN = 0,

SEARCHED_AND_LOCKED = 0, and the state leaves STATUS-BEAM_ON.

Clear the cause and press the matching reset. Expect: the contactors stay 0.

Confirm only a complete new §4 search brings them back. Do this once for a door

trip and once for a beam‑off‑button trip.

__________________________________________________

## 6 · The alarm / diagnostic layer (pages 162–174) — it watches, it does not trip

Idea: around the safety functions sits a layer that just tells the operator why something happened. It does not trip anything. Examples: per‑sensor alarm flags such as BL10E-PS-IT-01_ALARM (made from IT-01_TRIP through an off‑delay timer E_SOURCE_TIME = 120 s, page 172); the two‑channel discrepancy alarms (pages 171, 173–174); and system diagnostics (power‑supply, fan and network‑switch faults, force flags, module errors — Diagnostics, pages 241–250).

Sample check:

Force BL10E-PS-IT-01_TRIP = 1 and hold it for more than 120 s. Expect: the

alarm IT-01_ALARM comes on; clear the trip and it goes off after the 120 s timer.

Force BL10E-PS-GADC-01 = 0 on its own for longer than the voter's delay.

Expect: the voter's Dev (disagreement) flag comes on — a maintenance alarm,    not a trip.

__________________________________________________

## 7 · Coverage checklist (tick each when done)

| Tick | What you tested | Page | The idea it proves |
| --- | --- | --- | --- |
| ☐ | analogue sensor → trip flag (Way B) | 184–187 | set‑point + hysteresis |
| ☐ | two‑channel + discrepancy | 152–161, 171–174 | a wiring fault is not a trip |
| ☐ | SIF‑01 main door | 291 | 2oo3 voting |
| ☐ | SIF‑13 gate | 382 | 2oo3 + 200 ms |
| ☐ | SIF‑02 service door | 297 | 2oo3 or 1oo2 |
| ☐ | SIF‑03 current + voltage / unlock permit | 303 | two 2oo3 checks, 20 s, manual button |
| ☐ | SIF‑05 start permit (5 negative tests) | 344 | every start condition is required |
| ☐ | SIF‑06 search‑complete proof | 350 | doors shut at the final button |
| ☐ | SIF‑07 lock proof + 180 s (positive and negative) | 356 | command is not the same as confirmation |
| ☐ | SIF‑08 beam‑off buttons × 8 | 363 | 1oo7, latch, escape unlock |
| ☐ | SIF‑09 radiation × 4 signals | 368 | 1oo2, latch |
| ☐ | SIF‑10 enable key | 372 | 1oo1, key is not a reset |
| ☐ | SIF‑11 oxygen × 4 | 377 | 1oo4, latch |
| ☐ | full search T1→T8 | 326–338 | the search walk‑through |
| ☐ | 8 abort tests | 328–331 | both clocks + the monitors |
| ☐ | key‑trap release | 337 | search integrity |
| ☐ | "no silent restart" memory | 267 | the master safety rule |
| ☐ | alarm layer | 162–174 | watching vs protecting |

## 8 · Honest limits (read before you rely on a result)

The analogue set‑points are fixed fail‑safe numbers (OXMON_SP = 25.0,

IT/VT_SP = 0.0) — they cannot be forced; use §0.4. The example values used in the   other documents (19.5 % oxygen, "above 4 mA") come from the Cause & Effect matrix,   not from the program.

A few exact wire polarities are hard to read from the flattened program printout —

trust the live value you see in simulation; that is what offline simulation is for.

The full requirements document (TDI-PSS-SRS-0002) and the logic drawing

(Dwg 1224211) are not in this repo. For real plant work, check against them   (for example the C&E mentions 12 s where the program uses DOOR_UNLOCK_DELAY = 20 s).

## 9 · Test record (copy one per test)

Test (checklist row): ____   Page: ____   Date: ____   Engineer: ____
Started from §1 (STATUS-OPEN_READY = 1)?   Yes / No
Way A or Way B for analogue (§0.4):  ____
Forced (tag = value): ______________________________________
Watched (tag : value seen): ________________________________
Output (tag : value seen): _________________________________
Did it latch?  Reset used: ___________   New search needed?  Yes / No
PASS / FAIL: ____   Notes: __________________________________